## Setup
CLX IP	192.168.2.222

Tag Start	C10	First cell where TagName occurs on each sheet
Parameter Cell	E10	First cell where tag values are located
Parameter Names Cell	E7	Where parameter names start (Cfg_)

## L_ChangeDet
	L_ChangeDet: Logix Change Detector	Read From CLX:
		Send To CLX:

		Description:		Process Area for security	Update (poll) time for change data (1.0 to 60.0 sec)
		Usage:		Local	Input
		Data Type:		STRING_Area	REAL
			(Origin)	.Cfg_	.Cfg_
Unit	Tag Description	TagName	Instance	Area	UpdateT
		Default Values:	0	area01	5
		ChangeDet	1	area01	5

## L_CPU
	L_CPU: Logix CPU Utilization	Read From CLX:
		Send To CLX:

		Description:		Process Area for security	RSLogix 5000 S/N or Support Contract ID	Instance Number of Continuous Task if it exists (1..31) (set to 0 if none)	Controller Slot Number in local chassis	Update (poll) time for CPU data (sec)	Window Time for collecting Task data (sec)
		Usage:		Local	Local	Input	Input	Input	Input
		Data Type:		STRING_Area	STRING_40	DINT	DINT	REAL	REAL
			(Origin)	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_
Unit	Tag Description	TagName	Instance	Area	SupportInfo	ContTaskInstance	SlotNumber	UpdateT	WindowT
		Default Values:	0	area01	Enter Software S/N or Support Contract #	0	0	5	1
		L_CPU	1	area01	Enter Software S/N or Support Contract #	0	2	5	1.0

## L_Redun
	L_Redun: Controller Redundancy Monitor	Read From CLX:
		Send To CLX:

		Description:		Description for display on HMI	Label for graphic symbol displayed on HMI	Tagname for display on HMI	Process Area for security	Description of Chassis A Location	Description of Chassis B Location	1=Allow OCmd_Sync to initiate sync of primary to secondary	1=Allow MCmd_Switchover to initiate switch to secondary	Selects which chassis is A and which is B; if reversed on HMI, flip this bit	Number of slots in redundant chassis (4, 7, 10, 13, 17)	Type of Module in Slot 0 (0=filler, 1=CLx, 2=SRM, 3=RM, 4=CNet, 5=ENet	Type of Module in Slot 1 (0=filler, 1=CLx, 2=SRM, 3=RM, 4=CNet, 5=ENet	Type of Module in Slot 2 (0=filler, 1=CLx, 2=SRM, 3=RM, 4=CNet, 5=ENet	Type of Module in Slot 3 (0=filler, 1=CLx, 2=SRM, 3=RM, 4=CNet, 5=ENet	Type of Module in Slot 4 (0=filler, 1=CLx, 2=SRM, 3=RM, 4=CNet, 5=ENet	Type of Module in Slot 5 (0=filler, 1=CLx, 2=SRM, 3=RM, 4=CNet, 5=ENet	Type of Module in Slot 6 (0=filler, 1=CLx, 2=SRM, 3=RM, 4=CNet, 5=ENet	Type of Module in Slot 7 (0=filler, 1=CLx, 2=SRM, 3=RM, 4=CNet, 5=ENet	Type of Module in Slot 8 (0=filler, 1=CLx, 2=SRM, 3=RM, 4=CNet, 5=ENet	Type of Module in Slot 9 (0=filler, 1=CLx, 2=SRM, 3=RM, 4=CNet, 5=ENet	Type of Module in Slot 10 (0=filler, 1=CLx, 2=SRM, 3=RM, 4=CNet, 5=ENet	Type of Module in Slot 11 (0=filler, 1=CLx, 2=SRM, 3=RM, 4=CNet, 5=ENet	Type of Module in Slot 12 (0=filler, 1=CLx, 2=SRM, 3=RM, 4=CNet, 5=ENet	Type of Module in Slot 13 (0=filler, 1=CLx, 2=SRM, 3=RM, 4=CNet, 5=ENet	Type of Module in Slot 14 (0=filler, 1=CLx, 2=SRM, 3=RM, 4=CNet, 5=ENet	Type of Module in Slot 15 (0=filler, 1=CLx, 2=SRM, 3=RM, 4=CNet, 5=ENet	Type of Module in Slot 16 (0=filler, 1=CLx, 2=SRM, 3=RM, 4=CNet, 5=ENet	1=Sec.Not Ready Alarm exists and will be checked	1=Sec. Not Ready Alarm is latched in, requires Reset Command to clear	1=Sec. Not Ready Alarm must be acknowledged	Sec. Not Ready Alarm Severity: 1=info, 2=warn, 3=excep, 4=fault	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	Secondary Not Ready Alarm Condition	Secondary Not Ready Alarm Tag
		Usage:		Local	Local	Local	Local	Local	Local	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Local	Local	Local	Local	Local	Local
		Data Type:		STRING_40	STRING_20	STRING_20	STRING_Area	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	SINT	SINT	SINT	SINT	SINT	SINT	SINT	SINT	SINT	SINT	SINT	SINT	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20
			(Origin)	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.SecNotRdy.Cfg_	.SecNotRdy.Cfg_	.SecNotRdy.Cfg_	.SecNotRdy.Cfg_	.SecNotRdy.Cfg_	.SecNotRdy.Cfg_
Unit	Tag Description	TagName	Instance	Desc	Label	Tag	Area	ChasALoc	ChasBLoc	AllowOCmdSync	AllowMCmdSwitchover	Select_A_B	RackSize	Slot00	Slot01	Slot02	Slot03	Slot04	Slot05	Slot06	Slot07	Slot08	Slot09	Slot10	Slot11	Slot12	Slot13	Slot14	Slot15	Slot16	HasSecNotRdyAlm	SecNotRdyResetReqd	SecNotRdyAckReqd	SecNotRdySeverity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag
		Default Values:	0	Logix Controller Redundancy Monitor	Redundant Controller	L_Redun	area01	Upper Chassis	Lower Chassis	1	0	0	7	5	1	3	4	0	0	0	0	0	0	0	0	0	0	0	0	1	0	1	500	0	1	5	480	Secondary Not Ready	L_Redun.SecNotRdy
		L_Redun	1	Logix Controller Redundancy Monitor	Redundant Controller	L_Redun	area01	Upper Chassis	Lower Chassis	1	0	0	7	5	1	3	4	0	0	0	0	0	0	0	0	0	0	0	0	1	0	1	500	1	1	5	480	Secondary Not Ready	L_Redun.SecNotRdy
				Strings too long to fit are formatted like this

## L_TaskMon
	L_TaskMon: Logix Task Monitor	Read From CLX:
		Send To CLX:

		Description:		Process Area for security	Expected Execution Time of Task (including interrupts) (ms)	1=Task Plan Exceeded Alarm exists and will be checked	1=Task Plan Exceeded Alarm is latched in, requires Reset Command to clear	1=Task Plan Exceeded Alarm must be acknowledged	Task Plan Exceeded Alarm Severity: 1=info, 2=warn, 3=excep, 4=fault	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	Over Plan Alarm Condition	Over Plan Alarm Tag
		Usage:		Local	Input	Input	Input	Input	Input	Local	Local	Local	Local	Local	Local
		Data Type:		STRING_Area	REAL	BOOL	BOOL	BOOL	SINT	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20
			(Origin)	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.OverPlan.Cfg_	.OverPlan.Cfg_	.OverPlan.Cfg_	.OverPlan.Cfg_	.OverPlan.Cfg_	.OverPlan.Cfg_
Unit	Tag Description	TagName	Instance	Area	PlanExecT	HasOverPlanAlm	OverPlanResetReqd	OverPlanAckReqd	OverPlanSeverity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag
		Default Values:	0	area01	3000	1	0	1	750	0	1	5	480	Scan Time Over Plan	L_TaskMon.OverPlan
		L_TaskMonitor[0]	1	area01	40	1	0	1	750	1	1	5	480	Scan Time Over Plan	L_TaskMonitor[0]
		L_TaskMonitor[1]	2	area01	80	1	0	1	750	1	1	5	480	Scan Time Over Plan	L_TaskMonitor[1]
		L_TaskMonitor[2]	3	area01	200	1	0	1	750	1	1	5	480	Scan Time Over Plan	L_TaskMonitor[2]
		L_TaskMonitor[3]	4	area01	400	1	0	1	750	1	1	5	480	Scan Time Over Plan	L_TaskMonitor[3]
		L_TaskMonitor[4]	5		800	1	0	1	750	1	1	5	480	Scan Time Over Plan	L_TaskMonitor[4]
		L_TaskMonitor[5]	6	area01	1600	1	0	1	750	1	1	5	480	Scan Time Over Plan	L_TaskMonitor[5]
		L_TaskMonitor[6]	7	area01	4000	1	0	1	750	1	1	5	480	Scan Time Over Plan	L_TaskMonitor[6]
		L_TaskMonitor[7]	8	area01	8000	1	0	1	750	1	1	5	480	Scan Time Over Plan	L_TaskMonitor[7]

## P_AIChan
	P_AIChan: Analog Input Channel	Read From CLX:
		Send To CLX:

		Description:		Description for display on HMI	Label for graphic symbol displayed on HMI	Tagname for display on HMI	Process Area for security	Engineering Units for display on HMI	Signal Units for display on HMI	Input (unscaled) Minimum for Scaling (RU)	Input (unscaled) Maximum for Scaling (RU)	PV (Output) Minimum for Scaling (EU)	PV (Output) Maximum for Scaling (EU)	PV High Clamping Limit (EU)	PV Low Clamping Limit (EU)	Out-of-Range (fail) High Limit (Raw Units!)	Out-of-Range (fail) Low Limit (Raw Units!)	Out-of-Range (fail) High/Low Deadband (Raw Units!)	Minimum time Out of Range to raise Status (s)	Minimum time In Range to clear Out of Range Status (s)	Out-of-Range PV Action: 1=Use Input, 2=Hold Last Good, 3=Replace	Out-of-Range Flag as: 1=Good, 2=Uncertain, 3=Bad	Time with no change in Input to raise Stuck Status (s)	Stuck (unchanging) PV Action: 1=Use Input, 2=Hold Last Good, 3=Replace	Stuck (unchanging) Flag as: 1=Good, 2=Uncertain, 3=Bad	PV Not a Number PV Action: 1=Use Input, 2=Hold Last Good, 3=Replace	PV Not a Number Flag as: 1=Good, 2=Uncertain, 3=Bad	I/O Module Fault PV Action: 1=Use Input, 2=Hold Last Good, 3=Replace	I/O Module Fault Flag as: 1=Good, 2=Uncertain, 3=Bad	I/O Channel Fault PV Action: 1=Use Input, 2=Hold Last Good, 3=Replace	I/O Channel Fault Flag as: 1=Good, 2=Uncertain, 3=Bad	Inp_PVUncertain PV Action: 1=Use Input, 2=Hold Last Good, 3=Replace	Inp_PVUncertain Flag as: 1=Good, 2=Uncertain, 3=Bad	Function Check PV Action: 1=Use Input, 2=Hold Last Good, 3=Replace	Function Check Flag as: 1=Good, 2=Uncertain, 3=Bad	Maintenance Required PV Action: 1=Use Input, 2=Hold Last Good, 3=Replace	Maintenance Required Flag as: 1=Good, 2=Uncertain, 3=Bad	AOI Configuration Error PV Action: 1=Use Input, 2=Hold Last Good, 3=Replace	AOI Configuration Error Flag as: 1=Good, 2=Uncertain, 3=Bad	Value (EU) to use to replace PV when Action=Replace	1=Raise Sts_Fail (and alarm) if Bad or Uncertain quality, 0=only if Bad quality	1=Analog Input Failure Alarm exists and will be checked	1=Reset required to clear Analog InputFailure Alarm	1=Acknowledge required for Analog Input Failure Alarm	Failure Alarm Severity 1=info, 2=warn, 3=excep, 4=fault	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	Fail Alarm Condition	Fail Alarm Tag
		Usage:		Local	Local	Local	Local	Local	Local	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Local	Local	Local	Local	Local	Local
		Data Type:		STRING_40	STRING_20	STRING_20	STRING_Area	STRING_8	STRING_8	REAL	REAL	REAL	REAL	REAL	REAL	REAL	REAL	DINT	DINT	REAL	DINT	DINT	DINT	DINT	DINT	DINT	DINT	DINT	DINT	DINT	DINT	DINT	DINT	DINT	DINT	DINT	REAL	BOOL	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20
			(Origin)	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Fail.Cfg_	.Fail.Cfg_	.Fail.Cfg_	.Fail.Cfg_	.Fail.Cfg_	.Fail.Cfg_
Unit	Tag Description	TagName	Instance	Desc	Label	Tag	Area	EU	RU	InpRawMin	InpRawMax	PVEUMin	PVEUMax	PVHiLim	PVLoLim	InpOORHiLim	InpOORLoLim	InpOORDB	InpOOROnDly	InpOOROffDly	InpOORAction	InpOORQual	StuckT	InpStuckAction	InpStuckQual	InpNaNAction	InpNaNQual	ModFaultAction	ModFaultQual	ChanFaultAction	ChanFaultQual	OutOfSpecAction	OutOfSpecQual	FuncCheckAction	FuncCheckQual	MaintReqdAction	MaintReqdQual	CfgErrAction	CfgErrQual	PVReplaceVal	FailOnUncertain	HasFailAlm	FailResetReqd	FailAckReqd	FailSeverity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag
		Default Values:	0	Analog Channel Quality	Analog In Channel	P_AIChan	area01	%	mA DC	4	20	0	100	1.5E+038	-1.5E+038	20.733334	3.6666667	0.06666667	0	0	1	3	60	1	1	2	3	2	3	2	3	1	2	3	3	3	3	3	3	0	0	1	0	1	1000	1	1	5	480	Input Failure	P_AIChan.Fail
		MyP_AIn_Chan	1	Analog Channel Quality	Analog In Channel	FT101_Chan	area01	%	mA DC	4	20	0	100	1.50000000274888E+038	-1.50000000274888E+038	20.7333335876465	3.66666674613953	0.0666666701436043	0	0	1	3	60	1	1	2	3	2	3	2	3	1	2	3	3	3	3	3	3	0	0	1	0	1	3	1	1	5	480	Input Failure	P_AIChan.Fail
			2
			3
			4
			5
			6
			7
			8
			9
			10
			11
			12
			13
			14
			15
			16
			17
			18
			19
			20
			21
			22
			23
			24
			25
			26
			27
			28
			29
			30	Strings too long to fit are formatted like this
			31
			32
			33
			34
			35
			36
			37
			38
			39
			40
			41
			42
			43
			44
			45
			46
			47
			48
			49
			50
			51
			52
			53
			54
			55
			56
			57
			58
			59
			60
			61
			62
			63
			64
			65
			66
			67
			68
			69
			70
			71
			72
			73
			74
			75
			76
			77
			78
			79
			80
			81
			82
			83
			84
			85
			86
			87
			88
			89
			90
			91
			92
			93
			94
			95
			96
			97
			98
			99

## P_AIn
	P_AIn: Analog Input	Read From CLX:
		Send To CLX:

		Description:		Description for display on HMI	Label for graphic symbol displayed on HMI	Tagname for display on HMI	Process Area for security	Engineering Units for display on HMI	Input (unscaled) Minimum for Scaling	Input (unscaled) Maximum for Scaling	PV (Output) Minimum for Scaling to EU	PV (Output) Maximum for Scaling to EU	1=Tells HMI an object with more info is available	Number of decimal places for PV display (0..6)	PV Filter Time Constant (s), 0.0 = unfiltered	High-High Status Threshold (EU)	High-High Status Deadband (EU)	High Status Threshold (EU)	High Status Deadband (EU)	Low Status Threshold (EU)	Low Status Deadband (EU)	Low-Low Status Threshold (EU)	Low-Low Status Deadband (EU)	Out-of-Range (fail) High Limit (raw units)	Out-of-Range (fail) Low Limit (raw units)	Out-of-Range (fail) High/Low Deadband (raw units)	1=Disallow selection of Substitute PV	1=Tells HMI a Channel object (AIChan, etc.) is used for Inp_PV	1=Pass thru connected Channels SrcQ value, 0=generate SrcQ	1=High-High Alarm exists and will be checked	1=Reset required to clear High-High Alarm	1=Acknowledge required for High-High Alarm	High-High Alarm Severity 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	Minimum time above High-High Limit to raise Status (s)	Minimum time below High-High Limit (minus deadband) to clear Status (s)	High-High Status Gate Delay (s)	High-High Status Input Condition	High-High Status Gate Condition	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	High-High Alarm Condition	High-High Alarm Tag	1=High Alarm exists and will be checked	1=Reset required to clear High Alarm	1=Acknowledge required for High Alarm	High Alarm Severity 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	Minimum time above High Limit to raise Status (s)	Minimum time below High Limit (minus deadband) to clear Status (s)	High Status Gate Delay (s)	High Status Input Condition	High Status Gate Condition	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	High Alarm Condition	High Alarm Tag	1=Low Alarm exists and will be checked	1=Reset required to clear Low Alarm	1=Acknlowledge required for Low Alarm	Low Alarm Severity 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	Minimum time below Low Limit to raise Status (s)	Minimum time above Low Limit (plus deadband) to clear Status (s)	Low Status Gate Delay (s)	Low Status Input Condition	Low Status Gate Condition	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	Low Alarm Condition	Low Alarm Tag	1=Low-Low Alarm exists and will be checked	1=Reset required to clear Low-Low Alarm	1=Acknowledge required for Low-Low Alarm	Low-Low Alarm Severity 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	Minimum time below Low-Low Limit to raise Status (s)	Minimum time above Low-Low Limit (plus deadband) to clear Status (s)	Low-Low Status Gate Delay (s)	Lo-Lo Status Input Condition	Lo-Lo Status Gate Condition	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	Low-Low Alarm Condition	Low-Low Alarm Tag	1=Analog Input Failure Alarm exists and will be checked	1=Reset required to clear Analog InputFailure Alarm	1=Acknowledge required for Analog Input Failure Alarm	Failure Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	Minimum time Bad or Out of Range to raise Fail Status (s)	Minimum time OK or In Range to clear Fail Status (s)	Fail Status Gate Delay (s)	Fail Status Input Condition	Fail Status Gate Condition	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	Fail Alarm Condition	Fail Alarm Tag
		Usage:		Local	Local	Local	Local	Local	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Local	Local	Local	Local	Local	Local	Local	Local	Input	Input	Input	Input	Input	Input	Input	Local	Local	Local	Local	Local	Local	Local	Local	Input	Input	Input	Input	Input	Input	Input	Local	Local	Local	Local	Local	Local	Local	Local	Input	Input	Input	Input	Input	Input	Input	Local	Local	Local	Local	Local	Local	Local	Local	Input	Input	Input	Input	Input	Input	Input	Local	Local	Local	Local	Local	Local	Local	Local
		Data Type:		STRING_40	STRING_20	STRING_20	STRING_Area	STRING_8	REAL	REAL	REAL	REAL	BOOL	DINT	REAL	REAL	REAL	REAL	REAL	REAL	REAL	REAL	REAL	REAL	REAL	REAL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	DINT	REAL	REAL	REAL	STRING_20	STRING_20	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	REAL	REAL	REAL	STRING_20	STRING_20	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	REAL	REAL	REAL	STRING_20	STRING_20	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	REAL	REAL	REAL	STRING_20	STRING_20	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	REAL	REAL	REAL	STRING_20	STRING_20	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20
			(Origin)	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.HiHi.Cfg_	.HiHi.Cfg_	.HiHi.Cfg_	.HiHi.Cfg_	.HiHiGate.Cfg_	.HiHiGate.Cfg_	.HiHiGate.Cfg_	.HiHiGate.Cfg_	.HiHiGate.Cfg_	.HiHi.Cfg_	.HiHi.Cfg_	.HiHi.Cfg_	.HiHi.Cfg_	.HiHi.Cfg_	.HiHi.Cfg_	.Hi.Cfg_	.Hi.Cfg_	.Hi.Cfg_	.Hi.Cfg_	.HiGate.Cfg_	.HiGate.Cfg_	.HiGate.Cfg_	.HiGate.Cfg_	.HiGate.Cfg_	.Hi.Cfg_	.Hi.Cfg_	.Hi.Cfg_	.Hi.Cfg_	.Hi.Cfg_	.Hi.Cfg_	.Lo.Cfg_	.Lo.Cfg_	.Lo.Cfg_	.Lo.Cfg_	.LoGate.Cfg_	.LoGate.Cfg_	.LoGate.Cfg_	.LoGate.Cfg_	.LoGate.Cfg_	.Lo.Cfg_	.Lo.Cfg_	.Lo.Cfg_	.Lo.Cfg_	.Lo.Cfg_	.Lo.Cfg_	.LoLo.Cfg_	.LoLo.Cfg_	.LoLo.Cfg_	.LoLo.Cfg_	.LoLoGate.Cfg_	.LoLoGate.Cfg_	.LoLoGate.Cfg_	.LoLoGate.Cfg_	.LoLoGate.Cfg_	.LoLo.Cfg_	.LoLo.Cfg_	.LoLo.Cfg_	.LoLo.Cfg_	.LoLo.Cfg_	.LoLo.Cfg_	.Fail.Cfg_	.Fail.Cfg_	.Fail.Cfg_	.Fail.Cfg_	.FailGate.Cfg_	.FailGate.Cfg_	.FailGate.Cfg_	.FailGate.Cfg_	.FailGate.Cfg_	.Fail.Cfg_	.Fail.Cfg_	.Fail.Cfg_	.Fail.Cfg_	.Fail.Cfg_	.Fail.Cfg_
Unit	Tag Description	TagName	Instance	Desc	Label	Tag	Area	EU	InpRawMin	InpRawMax	PVEUMin	PVEUMax	HasMoreObj	PVDecPlcs	FiltTC	HiHiLim	HiHiDB	HiLim	HiDB	LoLim	LoDB	LoLoLim	LoLoDB	FailHiLim	FailLoLim	FailDB	NoSubstPV	HasChanObj	UseChanSrcQ	Exists	ResetReqd	AckReqd	Severity	OnDly	OffDly	GateDly	InpCond	GateCond	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	OnDly	OffDly	GateDly	InpCond	GateCond	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	OnDly	OffDly	GateDly	InpCond	GateCond	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	OnDly	OffDly	GateDly	InpCond	GateCond	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	OnDly	OffDly	GateDly	InpCond	GateCond	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag
		Default Values:	0	Analog Input	Analog Input	P_AIn	area01	%	0.0	100.0	0.0	100.0	0	2	0.0	1.50E+38	1	1.50E+38	1	-1.50E+38	1	-1.50E+38	1	103.958336	-2.0833333	0.41666666	0	0	0	0	0	1	750	0	0	0	PV High-High	Gating Condition	1	1	5	480	High-High Alarm	XAHH-nnnn	0	0	1	500	0	0	0	PV High	Gating Condition	1	1	5	480	High Alarm	XAH-nnnn	0	0	1	500	0	0	0	PV Low	Gating Condition	1	1	5	480	Low Alarm	XAL-nnnn	0	0	1	750	0	0	0	PV Low-Low	Gating Condition	1	1	5	480	Low-Low Alarm	XALL-nnnn	0	0	1	1000	0	0	0	Input Failure	Gating Condition	1	1	5	480	Input Failure	XAF-nnnn
		LE_600	1	Analog Input	Analog Input	LE-600	area01	%	0.0	100.0	0.0	100.0	True	2	0.0	1.5000000027488779e+38	1.0	1.5000000027488779e+38	1.0	-1.5000000027488779e+38	1.0	-1.5000000027488779e+38	1.0	103.95833587646484	-2.0833332538604736	0.4166666567325592	True	True	True	True	True	True	750	0.0	0.0	0.0	PV High-High	Gating Condition	True	True	5	0	High-High Alarm	P_Alarm	True	True	True	500	0.0	0.0	0.0	PV High	Gating Condition	True	True	5	0	High Alarm	P_Alarm	True	True	True	500	0.0	0.0	0.0	PV Low	Gating Condition	True	True	5	0	Low Alarm	P_Alarm	True	True	True	750	0.0	0.0	0.0	PV Low-Low	Gating Condition	True	True	5	0	Low-Low Alarm	P_Alarm	True	True	True	1000	0.0	0.0	0.0	Input Failure	Gating Condition	True	True	5	0	Input Failure	P_Alarm
		LE_601	2	Analog Input	Analog Input	LE-601	area01	%	0.0	100.0	0.0	100.0	True	2	0.0	1.5000000027488779e+38	1.0	1.5000000027488779e+38	1.0	-1.5000000027488779e+38	1.0	-1.5000000027488779e+38	1.0	103.95833587646484	-2.0833332538604736	0.4166666567325592	True	True	True	True	True	True	750	0.0	0.0	0.0	PV High-High	Gating Condition	True	True	5	0	High-High Alarm	P_Alarm	True	True	True	500	0.0	0.0	0.0	PV High	Gating Condition	True	True	5	0	High Alarm	P_Alarm	True	True	True	500	0.0	0.0	0.0	PV Low	Gating Condition	True	True	5	0	Low Alarm	P_Alarm	True	True	True	750	0.0	0.0	0.0	PV Low-Low	Gating Condition	True	True	5	0	Low-Low Alarm	P_Alarm	True	True	True	1000	0.0	0.0	0.0	Input Failure	Gating Condition	True	True	5	0	Input Failure	P_Alarm
		TE_601	3	Analog Input	Analog Input	TE-601	area01	%	0.0	100.0	0.0	100.0	False	2	0.0	1.5000000027488779e+38	1.0	1.5000000027488779e+38	1.0	-1.5000000027488779e+38	1.0	-1.5000000027488779e+38	1.0	103.95833587646484	-2.0833332538604736	0.4166666567325592	False	False	False	False	False	True	750	0.0	0.0	0.0	PV High-High	Gating Condition	True	True	5	0	High-High Alarm	P_Alarm	False	False	True	500	0.0	0.0	0.0	PV High	Gating Condition	True	True	5	0	High Alarm	P_Alarm	False	False	True	500	0.0	0.0	0.0	PV Low	Gating Condition	True	True	5	0	Low Alarm	P_Alarm	False	False	True	750	0.0	0.0	0.0	PV Low-Low	Gating Condition	True	True	5	0	Low-Low Alarm	P_Alarm	True	False	True	1000	0.0	0.0	0.0	Input Failure	Gating Condition	True	True	5	0	Input Failure	P_Alarm
		TE_602	4	Analog Input	Analog Input	TE-602	area01	%	0.0	100.0	0.0	100.0	False	2	0.0	1.5000000027488779e+38	1.0	1.5000000027488779e+38	1.0	-1.5000000027488779e+38	1.0	-1.5000000027488779e+38	1.0	103.95833587646484	-2.0833332538604736	0.4166666567325592	False	False	False	False	False	True	750	0.0	0.0	0.0	PV High-High	Gating Condition	True	True	5	0	High-High Alarm	P_Alarm	False	False	True	500	0.0	0.0	0.0	PV High	Gating Condition	True	True	5	0	High Alarm	P_Alarm	False	False	True	500	0.0	0.0	0.0	PV Low	Gating Condition	True	True	5	0	Low Alarm	P_Alarm	False	False	True	750	0.0	0.0	0.0	PV Low-Low	Gating Condition	True	True	5	0	Low-Low Alarm	P_Alarm	True	False	True	1000	0.0	0.0	0.0	Input Failure	Gating Condition	True	True	5	0	Input Failure	P_Alarm
		Template_P_AIn	5	Analog Input	Analog Input	P_AIn	area01	%	0.0	100.0	0.0	100.0	False	2	0.0	1.5000000027488779e+38	1.0	1.5000000027488779e+38	1.0	-1.5000000027488779e+38	1.0	-1.5000000027488779e+38	1.0	103.95833587646484	-2.0833332538604736	0.4166666567325592	False	False	False	False	False	True	750	0.0	0.0	0.0	PV High-High	Gating Condition	True	True	5	0	High-High Alarm	P_Alarm	False	False	True	500	0.0	0.0	0.0	PV High	Gating Condition	True	True	5	0	High Alarm	P_Alarm	False	False	True	500	0.0	0.0	0.0	PV Low	Gating Condition	True	True	5	0	Low Alarm	P_Alarm	False	False	True	750	0.0	0.0	0.0	PV Low-Low	Gating Condition	True	True	5	0	Low-Low Alarm	P_Alarm	False	False	True	1000	0.0	0.0	0.0	Input Failure	Gating Condition	True	True	5	0	Input Failure	P_Alarm
		LE_600A	6	Analog Input	Analog Input	LE-600A	area01	%	0.0	100.0	0.0	100.0	False	2	0.0	1.5000000027488779e+38	1.0	1.5000000027488779e+38	1.0	-1.5000000027488779e+38	1.0	-1.5000000027488779e+38	1.0	103.95833587646484	-2.0833332538604736	0.4166666567325592	False	False	False	False	False	True	750	0.0	0.0	0.0	PV High-High	Gating Condition	True	True	5	0	High-High Alarm	P_Alarm	False	False	True	500	0.0	0.0	0.0	PV High	Gating Condition	True	True	5	0	High Alarm	P_Alarm	False	False	True	500	0.0	0.0	0.0	PV Low	Gating Condition	True	True	5	0	Low Alarm	P_Alarm	False	False	True	750	0.0	0.0	0.0	PV Low-Low	Gating Condition	True	True	5	0	Low-Low Alarm	P_Alarm	True	False	True	1000	0.0	0.0	0.0	Input Failure	Gating Condition	True	True	5	0	Input Failure	P_Alarm
		LE_600B	7	Analog Input	Analog Input	LE-600B	area01	%	0.0	100.0	0.0	100.0	False	2	0.0	1.5000000027488779e+38	1.0	1.5000000027488779e+38	1.0	-1.5000000027488779e+38	1.0	-1.5000000027488779e+38	1.0	103.95833587646484	-2.0833332538604736	0.4166666567325592	False	False	False	False	False	True	750	0.0	0.0	0.0	PV High-High	Gating Condition	True	True	5	0	High-High Alarm	P_Alarm	False	False	True	500	0.0	0.0	0.0	PV High	Gating Condition	True	True	5	0	High Alarm	P_Alarm	False	False	True	500	0.0	0.0	0.0	PV Low	Gating Condition	True	True	5	0	Low Alarm	P_Alarm	False	False	True	750	0.0	0.0	0.0	PV Low-Low	Gating Condition	True	True	5	0	Low-Low Alarm	P_Alarm	True	False	True	1000	0.0	0.0	0.0	Input Failure	Gating Condition	True	True	5	0	Input Failure	P_Alarm
		LE_601A	8	Analog Input	Analog Input	LE-601A	area01	%	0.0	100.0	0.0	100.0	False	2	0.0	1.5000000027488779e+38	1.0	1.5000000027488779e+38	1.0	-1.5000000027488779e+38	1.0	-1.5000000027488779e+38	1.0	103.95833587646484	-2.0833332538604736	0.4166666567325592	False	False	False	False	False	True	750	0.0	0.0	0.0	PV High-High	Gating Condition	True	True	5	0	High-High Alarm	P_Alarm	False	False	True	500	0.0	0.0	0.0	PV High	Gating Condition	True	True	5	0	High Alarm	P_Alarm	False	False	True	500	0.0	0.0	0.0	PV Low	Gating Condition	True	True	5	0	Low Alarm	P_Alarm	False	False	True	750	0.0	0.0	0.0	PV Low-Low	Gating Condition	True	True	5	0	Low-Low Alarm	P_Alarm	True	False	True	1000	0.0	0.0	0.0	Input Failure	Gating Condition	True	True	5	0	Input Failure	P_Alarm
		LE_601B	9	Analog Input	Analog Input	LE-601B	area01	%	0.0	100.0	0.0	100.0	False	2	0.0	1.5000000027488779e+38	1.0	1.5000000027488779e+38	1.0	-1.5000000027488779e+38	1.0	-1.5000000027488779e+38	1.0	103.95833587646484	-2.0833332538604736	0.4166666567325592	False	False	False	False	False	True	750	0.0	0.0	0.0	PV High-High	Gating Condition	True	True	5	0	High-High Alarm	P_Alarm	False	False	True	500	0.0	0.0	0.0	PV High	Gating Condition	True	True	5	0	High Alarm	P_Alarm	False	False	True	500	0.0	0.0	0.0	PV Low	Gating Condition	True	True	5	0	Low Alarm	P_Alarm	False	False	True	750	0.0	0.0	0.0	PV Low-Low	Gating Condition	True	True	5	0	Low-Low Alarm	P_Alarm	True	False	True	1000	0.0	0.0	0.0	Input Failure	Gating Condition	True	True	5	0	Input Failure	P_Alarm
			10
			11
			12
			13
			14
			15
			16
			17
			18
			19
			20
			21
			22
			23
			24
			25
			26
			27
			28
			29	Strings too long to fit are formatted like this.
			30
			31
			32
			33
			34
			35
			36
			37
			38
			39
			40
			41
			42
			43
			44
			45
			46
			47
			48
			49
			50
			51
			52
			53
			54
			55
			56
			57
			58
			59
			60
			61
			62
			63
			64
			65
			66
			67
			68
			69
			70
			71
			72
			73
			74
			75
			76
			77
			78
			79
			80
			81
			82
			83
			84
			85
			86
			87
			88
			89
			90
			91
			92
			93
			94
			95
			96
			97
			98
			99

## P_AInAdv
	P_AInAdv: Advanced Analog Input	Read From CLX:
		Send To CLX:

		Description:		Description for display on HMI	Label for graphic symbol displayed on HMI	Tagname for display on HMI	Process Area for security	Engineering Units for display on HMI	Analog Reference for Deviation Alarms (EU)	1=Use Square Root characterization for DP to flow; 0=Linear	1=Enables the Rate of Change calc and HiRoC alarm	1=Enables Reference entry and Deviation calc and alarms	1=Disallow selection of Substitute PV	1=Tells HMI a Channel object (AIChan, etc.) is used for Inp_PV	1=Pass thru connected Channels SrcQ value, 0=generate SrcQ	Input (unscaled) Minimum for Scaling	Input (unscaled) Maximum for Scaling	PV (Output) Minimum for Scaling to EU	PV (Output) Maximum for Scaling to EU	1=Tells HMI an object with more info is available	Number of decimal places for PV display (0..6)	PV Rate of Change time base (sec) 60=/min, 3600=/hr	PV Filter Time Constant (sec), 0.0 = unfiltered	Current High-High Control Threshold (EU)	High-High Control Deadband (EU)	Current High Control Threshold (EU)	High Control Deadband (EU)	Current Low Control Threshold (EU)	Low Control Deadband (EU)	Current Low-Low Control Threshold (EU)	Low-Low Control Deadband (EU)	Current High-High Status Threshold	High-High Status Deadband (EU)	Current High Status Threshold	High Status Deadband (EU)	Current Low Status Threshold	Low Status Deadband (EU)	Current Low-Low Status Threshold	Low-Low Status Deadband (EU)	Current Rate of Change Status Threshold	High Rate of Change Status Deadband (EU)	Current High Deviation Status Threshold	High Deviation Status Deadband (EU)	Current Low Deviation Status Threshold	Low Deviation Status Deadband (EU)	Out-of-Range (fail) High Limit (RAW)	Out-of-Range (fail) Low Limit (RAW)	Out-of-Range (fail) High/Low Deadband (RAW)	High-High Status Input Condition	High-High Status Gate Condition	High-High Status Gate Delay (s)	Minimum time above High-High Limit to raise Status (sec)	Minimum time below High-High Limit (minus deadband) to clear Status (sec)	High-High Alarm Condition	High-High Alarm Tag	1=High-High Alarm exists and will be checked	1=Reset required to clear High-High Alarm	1=Acknowledge required for High-High Alarm	High-High Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	High Status Input Condition	High Status Gate Condition	High Status Gate Delay (s)	Minimum time above High Limit to raise Status (sec)	Minimum time below High Limit (minus deadband) to clear Status (sec)	High Alarm Condition	High Alarm Tag	1=High Alarm exists and will be checked	1=Reset required to clear High Alarm	1=Acknowledge required for High Alarm	High Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	Low Status Input Condition	Low Status Gate Condition	Low Status Gate Delay (s)	Minimum time below Low Limit to raise Status (sec)	Minimum time above Low Limit (plus deadband) to clear Status (sec)	Low Alarm Condition	Low Alarm Tag	1=Low Alarm exists and will be checked	1=Reset required to clear Low Alarm	1=Acknlowledge required for Low Alarm	Low Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	Lo-Lo Status Input Condition	Lo-Lo Status Gate Condition	Low-Low Status Gate Delay (s)	Minimum time below Low-Low Limit to raise Status (sec)	Minimum time above Low-Low Limit (plus deadband) to clear Status (sec)	Low-Low Alarm Condition	Low-Low Alarm Tag	1=Low-Low Alarm exists and will be checked	1=Reset required to clear Low-Low Alarm	1=Acknowledge required for Low-Low Alarm	Low-Low Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	High Rate of Change Status Input Condition	High Rate of Change Status Gate Condition	High Rate of Change Status Gate Delay (s)	Minimum time above High Rate of Change Limit to raise Status (sec)	Minimum time below High Rate of Change Limit (minus deadband) to clear Status (sec)	High Rate of Change Alarm Condition	High Rate of Change Alarm Tag	1=High Rate of Change Alarm exists and will be checked	1=Reset required to clear High Rate of Change Alarm	1=Acknowledge required for High Rate of Change Alarm	High Rate of Change Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved tHiRoCs long (min)	Hi Dev Status Input Condition	Hi Dev Status Gate Condition	High Deviation Status Gate Delay (s)	Minimum time above High Deviation Limit to raise Status (sec)	Minimum time below High Deviation Limit (minus deadband) to clear Status (sec)	High Deviation Alarm Condition	High Deviation Alarm Tag	1=High Deviation Alarm exists and will be checked	1=Reset required to clear High Deviation Alarm	1=Acknowledge required for High Deviation Alarm	High Deviation Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	Lo Dev Status Input Condition	Lo Dev Status Gate Condition	Low Deviation Status Gate Delay (s)	Minimum time above Low Deviation Limit to raise Status (sec)	Minimum time below Low Deviation Limit (minus deadband) to clear Status (sec)	Low Deviation Alarm Condition	Low Deviation Alarm Tag	1=Low Deviation Alarm exists and will be checked	1=Reset required to clear Low Deviation Alarm	1=Acknowledge required for Low Deviation Alarm	Low Deviation Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	Fail Status Input Condition	Fail Status Gate Condition	Fail Status Gate Delay (s)	Minimum time Bad or Out of Range to raise Fail Status (sec)	Minimum time OK or In Range to clear Fail Status (sec)	Fail Alarm Condition	Fail Alarm Tag	1=Analog Input Failure Alarm exists and will be checked	1=Reset required to clear Analog InputFailure Alarm	1=Acknowledge required for Analog Input Failure Alarm	Fail Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)
		Usage:		Local	Local	Local	Local	Local	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Local	Local	Input	Input	Input	Local	Local	Input	Input	Input	Input	Local	Local	Local	Local	Local	Local	Input	Input	Input	Local	Local	Input	Input	Input	Input	Local	Local	Local	Local	Local	Local	Input	Input	Input	Local	Local	Input	Input	Input	Input	Local	Local	Local	Local	Local	Local	Input	Input	Input	Local	Local	Input	Input	Input	Input	Local	Local	Local	Local	Local	Local	Input	Input	Input	Local	Local	Input	Input	Input	Input	Local	Local	Local	Local	Local	Local	Input	Input	Input	Local	Local	Input	Input	Input	Input	Local	Local	Local	Local	Local	Local	Input	Input	Input	Local	Local	Input	Input	Input	Input	Local	Local	Local	Local	Local	Local	Input	Input	Input	Local	Local	Input	Input	Input	Input	Local	Local	Local	Local
		Data Type:		STRING_40	STRING_20	STRING_20	STRING_Area	STRING_8	REAL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	REAL	REAL	REAL	REAL	BOOL	DINT	REAL	REAL	REAL	REAL	REAL	REAL	REAL	REAL	STRING_20	STRING_20	REAL	REAL	REAL	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	REAL	REAL	REAL	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	REAL	REAL	REAL	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	REAL	REAL	REAL	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	REAL	REAL	REAL	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	REAL	REAL	REAL	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	REAL	REAL	REAL	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	REAL	REAL	REAL	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT
			(Origin)	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.HiHiGate.Cfg_	.HiHiGate.Cfg_	.HiHiGate.Cfg_	.HiHiGate.Cfg_	.HiHiGate.Cfg_	.HiHi.Cfg_	.HiHi.Cfg_	.HiHi.Cfg_	.HiHi.Cfg_	.HiHi.Cfg_	.HiHi.Cfg_	.HiHi.Cfg_	.HiHi.Cfg_	.HiGate.Cfg_	.HiGate.Cfg_	.HiGate.Cfg_	.HiGate.Cfg_	.HiGate.Cfg_	.Hi.Cfg_	.Hi.Cfg_	.Hi.Cfg_	.Hi.Cfg_	.Hi.Cfg_	.Hi.Cfg_	.Hi.Cfg_	.Hi.Cfg_	.LoGate.Cfg_	.LoGate.Cfg_	.LoGate.Cfg_	.LoGate.Cfg_	.LoGate.Cfg_	.Lo.Cfg_	.Lo.Cfg_	.Lo.Cfg_	.Lo.Cfg_	.Lo.Cfg_	.Lo.Cfg_	.Lo.Cfg_	.Lo.Cfg_	.LoLoGate.Cfg_	.LoLoGate.Cfg_	.LoLoGate.Cfg_	.LoLoGate.Cfg_	.LoLoGate.Cfg_	.LoLo.Cfg_	.LoLo.Cfg_	.LoLo.Cfg_	.LoLo.Cfg_	.LoLo.Cfg_	.LoLo.Cfg_	.LoLo.Cfg_	.LoLo.Cfg_	.HiRoCGate.Cfg_	.HiRoCGate.Cfg_	.HiRoCGate.Cfg_	.HiRoCGate.Cfg_	.HiRoCGate.Cfg_	.HiRoC.Cfg_	.HiRoC.Cfg_	.HiRoC.Cfg_	.HiRoC.Cfg_	.HiRoC.Cfg_	.HiRoC.Cfg_	.HiRoC.Cfg_	.HiRoC.Cfg_	.HiDevGate.Cfg_	.HiDevGate.Cfg_	.HiDevGate.Cfg_	.HiDevGate.Cfg_	.HiDevGate.Cfg_	.HiDev.Cfg_	.HiDev.Cfg_	.HiDev.Cfg_	.HiDev.Cfg_	.HiDev.Cfg_	.HiDev.Cfg_	.HiDev.Cfg_	.HiDev.Cfg_	.LoDevGate.Cfg_	.LoDevGate.Cfg_	.LoDevGate.Cfg_	.LoDevGate.Cfg_	.LoDevGate.Cfg_	.LoDev.Cfg_	.LoDev.Cfg_	.LoDev.Cfg_	.LoDev.Cfg_	.LoDev.Cfg_	.LoDev.Cfg_	.LoDev.Cfg_	.LoDev.Cfg_	.FailGate.Cfg_	.FailGate.Cfg_	.FailGate.Cfg_	.FailGate.Cfg_	.FailGate.Cfg_	.Fail.Cfg_	.Fail.Cfg_	.Fail.Cfg_	.Fail.Cfg_	.Fail.Cfg_	.Fail.Cfg_	.Fail.Cfg_	.Fail.Cfg_
Unit	Tag Description	TagName	Instance	Desc	Label	Tag	Area	EU	Ref	UseSqRt	HasRoC	HasDev	NoSubstPV	HasChanObj	UseChanSrcQ	InpRawMin	InpRawMax	PVEUMin	PVEUMax	HasMoreObj	PVDecPlcs	RateTime	FiltTC	CtrlHiHiLim	CtrlHiHiDB	CtrlHiLim	CtrlHiDB	CtrlLoLim	CtrlLoDB	CtrlLoLoLim	CtrlLoLoDB	HiHiLim	HiHiDB	HiLim	HiDB	LoLim	LoDB	LoLoLim	LoLoDB	HiRoCLim	HiRoCDB	HiDevLim	HiDevDB	LoDevLim	LoDevDB	FailHiLim	FailLoLim	FailDB	InpCond	GateCond	GateDly	OnDly	OffDly	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	InpCond	GateCond	GateDly	OnDly	OffDly	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	InpCond	GateCond	GateDly	OnDly	OffDly	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	InpCond	GateCond	GateDly	OnDly	OffDly	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	InpCond	GateCond	GateDly	OnDly	OffDly	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	InpCond	GateCond	GateDly	OnDly	OffDly	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	InpCond	GateCond	GateDly	OnDly	OffDly	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	InpCond	GateCond	GateDly	OnDly	OffDly	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT
		Default Values:	0	Analog Input	Analog Input	P_AIn	area01	%	0	0	0	0	0	0	0	0.0	100.0	0.0	100.0	0	2	1.0	0.0	1.50E+38	1	1.50E+38	1	-1.50E+38	1	-1.50E+38	1	1.50E+38	1	1.50E+38	1	-1.50E+38	1	-1.50E+38	1	1.50E+38	1	1.50E+38	1	-1.50E+38	1	103.958336	-2.0833333	0.41666666	PV High-High	High-High Status Gate	0	0	0	PV High-High Alarm	P_AInAdv.HiHi	0	0	1	750	1	1	5	480	PV High Status	High Status Gate	0	0	0	PV High Alarm	P_AInAdv.Hi	0	0	1	500	1	1	5	480	PV Low Status	Low Status Gate	0	0	0	PV Low Alarm	P_AInAdv.Lo	0	0	1	500	1	1	5	480	PV Lo-Lo Status	Lo-Lo Status Gate	0	0	0	PV Low-Low Alarm	P_AInAdv.LoLo	0	0	1	750	1	1	5	480	PV Hi Rate of Change	Rate of Change Gate	0	0	0	High Rate of Change	P_AInAdv.HiRoC	0	0	1	500	1	1	5	480	PV Hi Dev Status	Hi Dev Status Gate	0	0	0	PV High Dev Alarm	P_AInAdv.HiDev	0	0	1	500	1	1	5	480	PV Lo Dev Status	Lo Dev Status Gate	0	0	0	PV Low Dev Alarm	P_AInAdv.LoDev	0	0	1	500	1	1	5	480	PV Fail Status	Fail Status Gate	0	0	0	PV Fail Alarm	P_AInAdv.Fail	0	0	1	1000	1	1	5	480
		MyP_AInAdv	1	Refinery Pipeline Flow	Refinery Flow	FI-1336	area01	Bbl/Day	0	1	1	1	0	1	0	0	100	0	37.0833320617676	0	2	1	0	1.50000000274888E+038	0.5	1.50000000274888E+038	0.5	-1.50E+38	0.5	-1.50E+38	0.5	1.50000000274888E+038	0.5	1.50000000274888E+038	0.5	-1.50E+38	0.5	-1.50E+38	0.5	1.50000000274888E+038	0.200000002980232	1.50000000274888E+038	0.200000002980232	-1.50E+38	0.200000002980232	37.5999984741211	-0.5	0.100000001490116	PV High-High	High-High Status Gat	0	0	0	PV High-High	P_AInAdv.HiHi	1	0	1	3	1	1	5	480	PV High Status	High Status Gate	0	0	0	PV High	P_AInAdv.Hi	1	0	1	2	1	1	5	480	PV Low Status	Low Status Gate	0	0	0	PV Low	P_AInAdv.Lo	1	0	1	3	1	1	5	480	PV Lo-Lo Status	Lo-Lo Status Gate	0	0	0	PV Low-Low	P_AInAdv.LoLo	1	0	1	3	1	1	5	480	PV Hi Rate of Change	Rate of Change Gate	0	0	0	High Rate of Change	P_AInAdv.HiRoC	1	0	1	2	1	1	5	480	PV Hi Dev Status	Hi Dev Status Gate	0	0	0	Deviation High	P_AInAdv.HiDev	1	0	1	3	1	1	5	480	PV Lo Dev Status	Lo Dev Status Gate	0	0	0	Deviation Low	P_AInAdv.LoDev	1	0	1	3	1	1	5	480	PV Fail Status	Fail Status Gate	0	0	0	Input Failure	P_AInAdv.Fail	1	0	1	3	1	1	5	480
			2
			3
			4
			5
			6
			7
			8
			9
			10
			11
			12
			13
			14
			15
			16
			17
			18
			19
			20
			21
			22
			23
			24
			25
			26
			27
			28
			29
			30	Strings too long to fit are formatted like this.
			31
			32
			33
			34
			35
			36
			37
			38
			39
			40
			41
			42
			43
			44
			45
			46
			47
			48
			49
			50
			51
			52
			53
			54
			55
			56
			57
			58
			59
			60
			61
			62
			63
			64
			65
			66
			67
			68
			69
			70
			71
			72
			73
			74
			75
			76
			77
			78
			79
			80
			81
			82
			83
			84
			85
			86
			87
			88
			89
			90
			91
			92
			93
			94
			95
			96
			97
			98
			99

## P_AInDual
	P_AInDual: Dual Analog Input	Read From CLX:
		Send To CLX:

		Description:		Description for display on HMI	Label for graphic symbol displayed on HMI	Tagname for display on HMI	Process Area for security	Engineering Units for display on HMI	Tagname for Sensor/ Input A for display on HMI	Tagname for Sensor/ Input B for display on HMI	Input (unscaled) Minimum for Scaling	Input (unscaled) Maximum for Scaling	PV (Output) Minimum for Scaling to EU	PV (Output) Maximum for Scaling to EU	1=Tells HMI an object with more info is available	Number of decimal places for PV display (0..6)	PV Filter Time Constant (sec), 0.0 = unfiltered	1=Disallow selection of Substitute PV	1=PSets track OSets in Oper, OSets track PSets in Prog, 0=no tracking	1=Tells HMI a Channel object (AIChan, etc.) is used for Inp_PVA	1=Tells HMI a Channel object (AIChan, etc.) is used for Inp_PVB	1=Pass thru connected Channel As SrcQ value, 0=generate SrcQ	1=Pass thru connected Channel Bs SrcQ value, 0=generate SrcQ	Current High-High Status Threshold	High-High Status Deadband (EU)	High-High Status Input Condition	High-High Status Gate Condition	High-High Status Gate Delay (s)	Minimum time above High-High Limit to raise Status (sec)	Minimum time below High-High Limit (minus deadband) to clear Status (sec)	High-High Alarm Condition	High-High Alarm Tag	1=High-High Alarm exists and will be checked	1=Reset required to clear High-High Alarm	1=Acknowledge required for High-High Alarm	High-High Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	Current High Status Threshold	High Status Deadband (EU)	High Status Input Condition	High Status Gate Condition	High Status Gate Delay (s)	Minimum time above High Limit to raise Status (sec)	Minimum time below High Limit (minus deadband) to clear Status (sec)	High Alarm Condition	High Alarm Tag	1=High Alarm exists and will be checked	1=Reset required to clear High Alarm	1=Acknowledge required for High Alarm	High Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	Current Low Status Threshold	Low Status Deadband (EU)	Low Status Input Condition	Low Status Gate Condition	Low Status Gate Delay (s)	Minimum time below Low Limit to raise Status (sec)	Minimum time above Low Limit (plus deadband) to clear Status (sec)	Low Alarm Condition	Low Alarm Tag	1=Low Alarm exists and will be checked	1=Reset required to clear Low Alarm	1=Acknlowledge required for Low Alarm	Low Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	Current Low-Low Status Threshold	Low-Low Status Deadband (EU)	Lo-Lo Status Input Condition	Lo-Lo Status Gate Condition	Low-Low Status Gate Delay (s)	Minimum time below Low-Low Limit to raise Status (sec)	Minimum time above Low-Low Limit (plus deadband) to clear Status (sec)	Low-Low Alarm Condition	Low-Low Alarm Tag	1=Low-Low Alarm exists and will be checked	1=Reset required to clear Low-Low Alarm	1=Acknowledge required for Low-Low Alarm	Low-Low Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	Only One Good Signal Alarm Condition	Only One Good Signal Alarm Tag	1=Only One Good Signal Alarm exists and will be checked	1=Reset required to clear Only One Good Signal Alarm	1=Acknowledge required for Only One Good Signal Alarm	Only One Good Signal Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved tOneGoods long (min)	No Good Signal Alarm Condition	No Good Signal Alarm Tag	1=No Good Signal Alarm exists and will be checked	1=Reset required to clear No Good Signal Alarm	1=Acknowledge required for No Good Signal Alarm	No Good Signal Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	Signal Difference Status Limit (EU-absolute delta)	Signal Difference Status Deadband (EU-delta)	Signal Difference Status Input Condition	Signal Difference Status Gate Condition	Signal Difference Status Gate Delay (s)	Minimum time above Signal Difference Limit to raise Status (sec)	Minimum time below Signal Difference Limit (minus deadband) to clear Status (sec)	Signal Difference Alarm Condition	Signal Difference Alarm Tag	1=Signal Difference Alarm exists and will be checked	1=Reset required to clear Signal Difference Alarm	1=Acknowledge required for Signal Difference Alarm	Signal Difference Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	Out-of-Range (fail) High Limit (RAW)	Out-of-Range (fail) Low Limit (RAW)	Out-of-Range (fail) High/Low Deadband (RAW)	Fail Status Input Condition	Fail Status Gate Condition	Signal Fail Status Gate Delay (s)	Minimum time Bad or Out of Range to raise Fail Status (sec)	Minimum time OK or In Range to clear Fail Status (sec)	Fail Alarm Condition	Fail Alarm Tag	1=Analog Input Failure Alarm exists and will be checked	1=Reset required to clear Analog InputFailure Alarm	1=Acknowledge required for Analog Input Failure Alarm	Failure Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	Oper keeps control in Prog Mode: .0=PV Selection, .1=Thresholds	Prog keeps control in Oper Mode: .0=PV Selection, .1=Thresholds
		Usage:		Local	Local	Local	Local	Local	Local	Local	Input	Input	Input	Input	Input	Input	Input	Input	Local	Local	Input	Input	Input	Local	Local	Input	Input	Input	Input	Local	Local	Local	Local	Input	Input	Local	Local	Input	Input	Input	Local	Local	Input	Input	Input	Input	Local	Local	Local	Local	Input	Input	Local	Local	Input	Input	Input	Local	Local	Input	Input	Input	Input	Local	Local	Local	Local	Input	Input	Local	Local	Input	Input	Input	Local	Local	Input	Input	Input	Input	Local	Local	Local	Local	Local	Local	Input	Input	Input	Input	Local	Local	Local	Local	Local	Local	Input	Input	Input	Input	Local	Local	Local	Local	Input	Input	Local	Local	Input	Input	Input	Local	Local	Input	Input	Input	Input	Local	Local	Local	Local	Input	Input	Input	Local	Local	Input	Input	Input	Local	Local	Input	Input	Input	Input	Local	Local	Local	Local	Input	Input
		Data Type:		STRING_40	STRING_20	STRING_20	STRING_Area	STRING_8	STRING_20	STRING_20	REAL	REAL	REAL	REAL	BOOL	DINT	REAL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	REAL	REAL	STRING_20	STRING_20	REAL	REAL	REAL	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	REAL	REAL	STRING_20	STRING_20	REAL	REAL	REAL	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	REAL	REAL	STRING_20	STRING_20	REAL	REAL	REAL	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	REAL	REAL	STRING_20	STRING_20	REAL	REAL	REAL	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	REAL	REAL	STRING_20	STRING_20	REAL	REAL	REAL	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	REAL	REAL	REAL	STRING_20	STRING_20	REAL	REAL	REAL	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	SINT	SINT
			(Origin)	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.HiHiGate.Cfg_	.HiHiGate.Cfg_	.HiHiGate.Cfg_	.HiHiGate.Cfg_	.HiHiGate.Cfg_	.HiHi.Cfg_	.HiHi.Cfg_	.HiHi.Cfg_	.HiHi.Cfg_	.HiHi.Cfg_	.HiHi.Cfg_	.HiHi.Cfg_	.HiHi.Cfg_	.Cfg_	.Cfg_	.HiGate.Cfg_	.HiGate.Cfg_	.HiGate.Cfg_	.HiGate.Cfg_	.HiGate.Cfg_	.Hi.Cfg_	.Hi.Cfg_	.Hi.Cfg_	.Hi.Cfg_	.Hi.Cfg_	.Hi.Cfg_	.Hi.Cfg_	.Hi.Cfg_	.Cfg_	.Cfg_	.LoGate.Cfg_	.LoGate.Cfg_	.LoGate.Cfg_	.LoGate.Cfg_	.LoGate.Cfg_	.Lo.Cfg_	.Lo.Cfg_	.Lo.Cfg_	.Lo.Cfg_	.Lo.Cfg_	.Lo.Cfg_	.Lo.Cfg_	.Lo.Cfg_	.Cfg_	.Cfg_	.LoLoGate.Cfg_	.LoLoGate.Cfg_	.LoLoGate.Cfg_	.LoLoGate.Cfg_	.LoLoGate.Cfg_	.LoLo.Cfg_	.LoLo.Cfg_	.LoLo.Cfg_	.LoLo.Cfg_	.LoLo.Cfg_	.LoLo.Cfg_	.LoLo.Cfg_	.LoLo.Cfg_	.OneGood.Cfg_	.OneGood.Cfg_	.OneGood.Cfg_	.OneGood.Cfg_	.OneGood.Cfg_	.OneGood.Cfg_	.OneGood.Cfg_	.OneGood.Cfg_	.NoneGood.Cfg_	.NoneGood.Cfg_	.NoneGood.Cfg_	.NoneGood.Cfg_	.NoneGood.Cfg_	.NoneGood.Cfg_	.NoneGood.Cfg_	.NoneGood.Cfg_	.Cfg_	.Cfg_	.DiffGate.Cfg_	.DiffGate.Cfg_	.DiffGate.Cfg_	.DiffGate.Cfg_	.DiffGate.Cfg_	.Diff.Cfg_	.Diff.Cfg_	.Diff.Cfg_	.Diff.Cfg_	.Diff.Cfg_	.Diff.Cfg_	.Diff.Cfg_	.Diff.Cfg_	.Cfg_	.Cfg_	.Cfg_	.FailGate.Cfg_	.FailGate.Cfg_	.FailGate.Cfg_	.FailGate.Cfg_	.FailGate.Cfg_	.Fail.Cfg_	.Fail.Cfg_	.Fail.Cfg_	.Fail.Cfg_	.Fail.Cfg_	.Fail.Cfg_	.Fail.Cfg_	.Fail.Cfg_	.Cfg_	.Cfg_
Unit	Tag Description	TagName	Instance	Desc	Label	Tag	Area	EU	PVATag	PVBTag	InpRawMin	InpRawMax	PVEUMin	PVEUMax	HasMoreObj	PVDecPlcs	FiltTC	NoSubstPV	SetTrack	HasChanObjA	HasChanObjB	UseChanSrcQA	UseChanSrcQB	HiHiLim	HiHiDB	InpCond	GateCond	GateDly	OnDly	OffDly	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	HiLim	HiDB	InpCond	GateCond	GateDly	OnDly	OffDly	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	LoLim	LoDB	InpCond	GateCond	GateDly	OnDly	OffDly	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	LoLoLim	LoLoDB	InpCond	GateCond	GateDly	OnDly	OffDly	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	DiffLim	DiffDB	InpCond	GateCond	GateDly	OnDly	OffDly	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	FailHiLim	FailLoLim	FailDB	InpCond	GateCond	GateDly	OnDly	OffDly	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	OperKeep	ProgKeep
		Default Values:	0	Dual Analog Input	Analog Input	P_AInDual	area01	%	Sensor / Input A	Sensor / Input B	0.0	100.0	0.0	100.0	0	2	0.0	0	0	0	0	0	0	1.50E+38	1.0	PV High-High	Hi-Hi Status Gate	0	0	0	PV High-High Alarm	P_AInDual.HiHi	0	0	1	750	1	1	5	480	1.50E+38	1	PV High Status	High Status Gate	0	0	0	PV High Alarm	P_AInDual.Hi	0	0	1	500	1	1	5	480	-1.50E+38	1.0	PV Low Status	Low Status Gate	0	0	0	PV Low Alarm	P_AInDual.Lo	0	0	1	500	1	1	5	480	-1.50E+38	1.0	PV Lo-Lo Status	Lo-Lo Status Gate	0	0	0	PV Low-Low Alarm	P_AInDual.LoLo	0	0	1	750	1	1	5	480	Only One Good Input	P_AInDual.OneGood	0	0	1	500	1	1	5	480	No Good Input	P_AInDual.NoneGood	0	0	1	500	1	1	5	480	1.50E+38	1	Hi Signal Difference	Signal Diff. Gate	0	0	0	Signal Diff Alarm	P_AInDual.Diff	0	0	1	500	1	1	5	480	103.958336	-2.0833333	0.41666666	PV Fail Status	Fail Status Gate	0	0	0	PV Fail Alarm	P_AInDual.Fail	0	0	1	1000	1	1	5	480	2#0000_0000	2#0000_0000
		MyP_AInDual	1	Bioreactor 1 pH (Dual Probe)	Bioreactor 1	AI101	area01	pH	AIT-101 A	AIT-101 B	0	100	0	14	0	2	0	0	0	0	0	0	0	1.50000000274888E+038	0.200000002980232	PV High-High	Hi-Hi Status Gate	0	0	0	PV High-High	FI102AB.HiHi	1	0	1	3	1	1	5	480	1.50000000274888E+038	0.200000002980232	PV High Status	High Status Gate	0	0	0	PV High	FI102AB.Hi	1	0	1	3	1	1	5	480	-1.50E+38	0.200000002980232	PV Low Status	Low Status Gate	0	0	0	PV Low	FI102AB.Lo	1	0	1	3	1	1	5	480	-1.50E+38	0.200000002980232	PV Lo-Lo Status	Lo-Lo Status Gate	0	0	0	PV Low-Low	FI102AB.LoLo	1	0	1	3	1	1	5	480	Only One Good Input	FI102AB.OneGood	1	0	1	3	1	1	5	480	No Good Input	FI102AB.NoneGood	1	0	1	3	1	1	5	480	5.00E-01	0.200000002980232	Hi Signal Difference	Signal Diff. Gate	0	0	0	Hi Signal Difference	FI102AB.Diff	1	0	1	3	1	1	5	480	102	-2	0	PV Fail Status	Fail Status Gate	0	0	0	Input Failure	FI102AB.Fail	1	0	1	3	1	1	5	480	0	0
			2
			3
			4
			5
			6
			7
			8
			9
			10
			11
			12
			13
			14
			15
			16
			17
			18
			19
			20
			21
			22
			23
			24
			25
			26
			27
			28
			29
			30	Strings too long to fit are formatted like this.
			31
			32
			33
			34
			35
			36
			37
			38
			39
			40
			41
			42
			43
			44
			45
			46
			47
			48
			49
			50
			51
			52
			53
			54
			55
			56
			57
			58
			59
			60
			61
			62
			63
			64
			65
			66
			67
			68
			69
			70
			71
			72
			73
			74
			75
			76
			77
			78
			79
			80
			81
			82
			83
			84
			85
			86
			87
			88
			89
			90
			91
			92
			93
			94
			95
			96
			97
			98
			99

## P_AInFFR
	P_AInFFR: Analog Input from FOUNDATION	Read From CLX:
	Fieldbus via 1788-EN2FFR	Send To CLX:

		Description:		Description for display on HMI	Label for graphic symbol displayed on HMI	Tagname for display on HMI	Process Area for security	Engineering Units for display on HMI	PV (Output) Minimum for Scaling to EU	PV (Output) Maximum for Scaling to EU	Number of decimal places for PV display (0..6)	PV Filter Time Constant (sec), 0.0 = unfiltered	Select PV to use for this AIn (1..8)	1=Tells HMI an object with more info is available	High-High Status Threshold (EU)	High-High Status Deadband (EU)	High Status Threshold (EU)	High Status Deadband (EU)	Low Status Threshold (EU)	Low Status Deadband (EU)	Low-Low Status Threshold (EU)	Low-Low Status Deadband (EU)	Out-of-Range (fail) High Limit (EU)	Out-of-Range (fail) Low Limit (EU)	Out-of-Range (fail) High/Low Deadband (EU)	1=Disallow selection of Substitute PV	1=High-High Alarm exists and will be checked	1=Reset required to clear High-High Alarm	1=Acknowledge required for High-High Alarm	High-High Alarm Severity 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	Minimum time above High-High Limit to raise Status (s)	Minimum time below High-High Limit (minus deadband) to clear Status (s)	High-High Status Gate Delay (s)	High-High Status Input Condition	High-High Status Gate Condition	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	High-High Alarm Condition	High-High Alarm Tag	1=High Alarm exists and will be checked	1=Reset required to clear High Alarm	1=Acknowledge required for High Alarm	High Alarm Severity 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	Minimum time above High Limit to raise Status (s)	Minimum time below High Limit (minus deadband) to clear Status (s)	High Status Gate Delay (s)	High Status Input Condition	High Status Gate Condition	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	High Alarm Condition	High Alarm Tag	1=Low Alarm exists and will be checked	1=Reset required to clear Low Alarm	1=Acknlowledge required for Low Alarm	Low Alarm Severity 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	Minimum time below Low Limit to raise Status (s)	Minimum time above Low Limit (plus deadband) to clear Status (s)	Low Status Gate Delay (s)	Low Status Input Condition	Low Status Gate Condition	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	Low Alarm Condition	Low Alarm Tag	1=Low-Low Alarm exists and will be checked	1=Reset required to clear Low-Low Alarm	1=Acknowledge required for Low-Low Alarm	Low-Low Alarm Severity 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	Minimum time below Low-Low Limit to raise Status (s)	Minimum time above Low-Low Limit (plus deadband) to clear Status (s)	Low-Low Status Gate Delay (s)	Lo-Lo Status Input Condition	Lo-Lo Status Gate Condition	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	Low-Low Alarm Condition	Low-Low Alarm Tag	1=Analog Input Failure Alarm exists and will be checked	1=Reset required to clear Analog InputFailure Alarm	1=Acknowledge required for Analog Input Failure Alarm	Failure Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	Minimum time Bad or Out of Range to raise Fail Status (s)	Minimum time OK or In Range to clear Fail Status (s)	Fail Status Gate Delay (s)	Fail Status Input Condition	Fail Status Gate Condition	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	Fail Alarm Condition	Fail Alarm Tag
		Usage:		Local	Local	Local	Local	Local	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Local	Local	Local	Local	Local	Local	Local	Local	Input	Input	Input	Input	Input	Input	Input	Local	Local	Local	Local	Local	Local	Local	Local	Input	Input	Input	Input	Input	Input	Input	Local	Local	Local	Local	Local	Local	Local	Local	Input	Input	Input	Input	Input	Input	Input	Local	Local	Local	Local	Local	Local	Local	Local	Input	Input	Input	Input	Input	Input	Input	Local	Local	Local	Local	Local	Local	Local	Local
		Data Type:		STRING_40	STRING_20	STRING_20	STRING_Area	STRING_8	REAL	REAL	DINT	REAL	DINT	BOOL	REAL	REAL	REAL	REAL	REAL	REAL	REAL	REAL	REAL	REAL	REAL	BOOL	BOOL	BOOL	BOOL	DINT	REAL	REAL	REAL	STRING_20	STRING_20	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	REAL	REAL	REAL	STRING_20	STRING_20	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	REAL	REAL	REAL	STRING_20	STRING_20	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	REAL	REAL	REAL	STRING_20	STRING_20	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	REAL	REAL	REAL	STRING_20	STRING_20	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20
			(Origin)	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.HiHi.Cfg_	.HiHi.Cfg_	.HiHi.Cfg_	.HiHi.Cfg_	.HiHiGate.Cfg_	.HiHiGate.Cfg_	.HiHiGate.Cfg_	.HiHiGate.Cfg_	.HiHiGate.Cfg_	.HiHi.Cfg_	.HiHi.Cfg_	.HiHi.Cfg_	.HiHi.Cfg_	.HiHi.Cfg_	.HiHi.Cfg_	.Hi.Cfg_	.Hi.Cfg_	.Hi.Cfg_	.Hi.Cfg_	.HiGate.Cfg_	.HiGate.Cfg_	.HiGate.Cfg_	.HiGate.Cfg_	.HiGate.Cfg_	.Hi.Cfg_	.Hi.Cfg_	.Hi.Cfg_	.Hi.Cfg_	.Hi.Cfg_	.Hi.Cfg_	.Lo.Cfg_	.Lo.Cfg_	.Lo.Cfg_	.Lo.Cfg_	.LoGate.Cfg_	.LoGate.Cfg_	.LoGate.Cfg_	.LoGate.Cfg_	.LoGate.Cfg_	.Lo.Cfg_	.Lo.Cfg_	.Lo.Cfg_	.Lo.Cfg_	.Lo.Cfg_	.Lo.Cfg_	.LoLo.Cfg_	.LoLo.Cfg_	.LoLo.Cfg_	.LoLo.Cfg_	.LoLoGate.Cfg_	.LoLoGate.Cfg_	.LoLoGate.Cfg_	.LoLoGate.Cfg_	.LoLoGate.Cfg_	.LoLo.Cfg_	.LoLo.Cfg_	.LoLo.Cfg_	.LoLo.Cfg_	.LoLo.Cfg_	.LoLo.Cfg_	.Fail.Cfg_	.Fail.Cfg_	.Fail.Cfg_	.Fail.Cfg_	.FailGate.Cfg_	.FailGate.Cfg_	.FailGate.Cfg_	.FailGate.Cfg_	.FailGate.Cfg_	.Fail.Cfg_	.Fail.Cfg_	.Fail.Cfg_	.Fail.Cfg_	.Fail.Cfg_	.Fail.Cfg_
Unit	Tag Description	TagName	Instance	Desc	Label	Tag	Area	EU	PVEUMin	PVEUMax	PVDecPlcs	FiltTC	PVSelect	HasMoreObj	HiHiLim	HiHiDB	HiLim	HiDB	LoLim	LoDB	LoLoLim	LoLoDB	FailHiLim	FailLoLim	FailDB	NoSubstPV	Exists	ResetReqd	AckReqd	Severity	OnDly	OffDly	GateDly	InpCond	GateCond	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	OnDly	OffDly	GateDly	InpCond	GateCond	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	OnDly	OffDly	GateDly	InpCond	GateCond	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	OnDly	OffDly	GateDly	InpCond	GateCond	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	OnDly	OffDly	GateDly	InpCond	GateCond	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag
		Default Values:	0	Analog Input (Foundation Fieldbus)'	Analog Input (FF)'	P_AInFFR'	area01	'%'	0.0	100.0	2	0.0	1	0	1.50E+38	1	1.50E+38	1	-1.50E+38	1	-1.50E+38	1	103.958336	-2.0833333	0.41666666	0	0	0	1	750	0	0	0	PV High-High	Gating Condition	1	1	5	480	High-High Alarm	XAHH-nnnn	0	0	1	500	0	0	0	PV High	Gating Condition	1	1	5	480	High Alarm	XAH-nnnn	0	0	1	500	0	0	0	PV Low	Gating Condition	1	1	5	480	Low Alarm	XAL-nnnn	0	0	1	750	0	0	0	PV Low-Low	Gating Condition	1	1	5	480	Low-Low Alarm	XALL-nnnn	0	0	1	1000	0	0	0	Input Failure	Gating Condition	1	1	5	480	Input Failure	XAF-nnnn
		MyP_AInFFR	1	Analog Input (Foundation Fieldbus)	Analog Input (FF)	EH_Cerabar S-XXXXXXX	area01	mBar	0	100	2	0	1	0	1.50000000274888E+038	1	1.50000000274888E+038	1	-1.50000000274888E+038	1	-1.50000000274888E+038	1	103.958335876465	-2.08333325386047	0.416666656732559	0	1	0	1	750	0	0	0	PV High-High	Gating Condition	1	1	5	480	High-High Alarm	XAHH-nnnn	1	0	1	500	0	0	0	PV High	Gating Condition	1	1	5	480	High Alarm	XAH-nnnn	1	0	1	500	0	0	0	PV Low	Gating Condition	1	1	5	480	Low Alarm	XAL-nnnn	1	0	1	750	0	0	0	PV Low-Low	Gating Condition	1	1	5	480	Low-Low Alarm	XALL-nnnn	1	0	1	1000	0	0	0	Input Failure	Gating Condition	1	1	5	480	Input Failure	XAF-nnnn
			2
			3
			4
			5
			6
			7
			8
			9
			10
			11
			12
			13
			14
			15
			16
			17
			18
			19
			20
			21
			22
			23
			24
			25
			26
			27
			28
			29	Strings too long to fit are formatted like this.
			30
			31
			32
			33
			34
			35
			36
			37
			38
			39
			40
			41
			42
			43
			44
			45
			46
			47
			48
			49
			50
			51
			52
			53
			54
			55
			56
			57
			58
			59
			60
			61
			62
			63
			64
			65
			66
			67
			68
			69
			70
			71
			72
			73
			74
			75
			76
			77
			78
			79
			80
			81
			82
			83
			84
			85
			86
			87
			88
			89
			90
			91
			92
			93
			94
			95
			96
			97
			98
			99

## P_AInHART
	P_AInHART: HART Analog Input	Read From CLX:
	(Channel object)	Send To CLX:

		Description:		Description for display on HMI	Label for graphic symbol displayed on HMI	Tagname for display on HMI	Process Area for security	Engineering Units for display on HMI	1=HART instrument, 0=non-HART (4-20 mA only) instrument	PV (Output) Minimum for Scaling to EU	PV (Output) Maximum for Scaling to EU	Number of decimal places for PV display (0..6)	PV Filter Time Constant (sec), 0.0 = unfiltered	1=Digital PV (primary variable) is configured	Label for Primary Variable for display on HMI	Engineering Units for HART PV display on HMI	1=Digital SV (secondary variable) is configured	Label for Secondary VarEngineering Units for HART SV display on HMIiable for display on HMI	Engineering Units for HART PV display on HMI	Number of decimal places for SV display (0..6)	1=Digital TV (third variable) is configured	Label for Third Variable for display on HMI	Engineering Units for HART TV display on HMI	Number of decimal places for FV display (0..6)	1=Digital FV (fourth variable) is configured	Label for Fourth Variable for display on HMI	Engineering Units for HART FV display on HMI	Number of decimal places for FV display (0..6)	1=Use HART text for Desc, Label, Tag, EU; 0=Manually entered	1=Use HART scaling for raw, EU ranges; 0=Manually entered ranges	1=Use HART digital status0=Manually entered ranges	1=automatically update device info, 0=no auto update	1=allow manual device info update request, 0=disallow	1=Tells HMI an object with more info is available	Input (unscaled) Minimum for Scaling	Input (unscaled) Maximum for Scaling	High-High Status Threshold (EU)	High-High Status Deadband (EU)	High Status Threshold (EU)	High Status Deadband (EU)	Low Status Threshold (EU)	Low Status Deadband (EU)	Low-Low Status Threshold (EU)	Low-Low Status Deadband (EU)	Out-of-Range (fail) High Limit (EU)	Out-of-Range (fail) Low Limit (EU)	Out-of-Range (fail) High/Low Deadband (EU)	1=Disallow selection of Substitute PV	1=High-High Alarm exists and will be checked	1=Reset required to clear High-High Alarm	1=Acknowledge required for High-High Alarm	High-High Alarm Severity 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	Minimum time above High-High Limit to raise Status (s)	Minimum time below High-High Limit (minus deadband) to clear Status (s)	High-High Status Gate Delay (s)	High-High Status Input Condition	High-High Status Gate Condition	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	High-High Alarm Condition	High-High Alarm Tag	1=High Alarm exists and will be checked	1=Reset required to clear High Alarm	1=Acknowledge required for High Alarm	High Alarm Severity 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	Minimum time above High Limit to raise Status (s)	Minimum time below High Limit (minus deadband) to clear Status (s)	High Status Gate Delay (s)	High Status Input Condition	High Status Gate Condition	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	High Alarm Condition	High Alarm Tag	1=Low Alarm exists and will be checked	1=Reset required to clear Low Alarm	1=Acknlowledge required for Low Alarm	Low Alarm Severity 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	Minimum time below Low Limit to raise Status (s)	Minimum time above Low Limit (plus deadband) to clear Status (s)	Low Status Gate Delay (s)	Low Status Input Condition	Low Status Gate Condition	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	Low Alarm Condition	Low Alarm Tag	1=Low-Low Alarm exists and will be checked	1=Reset required to clear Low-Low Alarm	1=Acknowledge required for Low-Low Alarm	Low-Low Alarm Severity 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	Minimum time below Low-Low Limit to raise Status (s)	Minimum time above Low-Low Limit (plus deadband) to clear Status (s)	Low-Low Status Gate Delay (s)	Lo-Lo Status Input Condition	Lo-Lo Status Gate Condition	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	Low-Low Alarm Condition	Low-Low Alarm Tag	1=Analog Input Failure Alarm exists and will be checked	1=Reset required to clear Analog InputFailure Alarm	1=Acknowledge required for Analog Input Failure Alarm	Failure Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	Minimum time Bad or Out of Range to raise Fail Status (s)	Minimum time OK or In Range to clear Fail Status (s)	Fail Status Gate Delay (s)	Fail Status Input Condition	Fail Status Gate Condition	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	Fail Alarm Condition	Fail Alarm Tag	1=Tells HMI a Channel object (AIChan, etc.) is used for Inp_PV	1=Pass thru connected Channels SrcQ value, 0=generate SrcQ
		Usage:		Local	Local	Local	Local	Local	Input	Input	Input	Input	Input	Input	Local	Local	Input	Local	Local	Input	Input	Local	Local	Input	Input	Local	Local	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Local	Local	Local	Local	Local	Local	Local	Local	Input	Input	Input	Input	Input	Input	Input	Local	Local	Local	Local	Local	Local	Local	Local	Input	Input	Input	Input	Input	Input	Input	Local	Local	Local	Local	Local	Local	Local	Local	Input	Input	Input	Input	Input	Input	Input	Local	Local	Local	Local	Local	Local	Local	Local	Input	Input	Input	Input	Input	Input	Input	Local	Local	Local	Local	Local	Local	Local	Local	Input	Input
		Data Type:		STRING_40	STRING_20	STRING_20	STRING_Area	STRING_8	BOOL	REAL	REAL	DINT	REAL	BOOL	STRING_16	STRING_8	BOOL	STRING_16	STRING_8	DINT	BOOL	STRING_16	STRING_8	DINT	BOOL	STRING_16	STRING_8	DINT	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	REAL	REAL	REAL	REAL	REAL	REAL	REAL	REAL	REAL	REAL	REAL	REAL	REAL	BOOL	BOOL	BOOL	BOOL	DINT	REAL	REAL	REAL	STRING_20	STRING_20	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	REAL	REAL	REAL	STRING_20	STRING_20	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	REAL	REAL	REAL	STRING_20	STRING_20	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	REAL	REAL	REAL	STRING_20	STRING_20	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	REAL	REAL	REAL	STRING_20	STRING_20	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	BOOL	BOOL
			(Origin)	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.HiHi.Cfg_	.HiHi.Cfg_	.HiHi.Cfg_	.HiHi.Cfg_	.HiHiGate.Cfg_	.HiHiGate.Cfg_	.HiHiGate.Cfg_	.HiHiGate.Cfg_	.HiHiGate.Cfg_	.HiHi.Cfg_	.HiHi.Cfg_	.HiHi.Cfg_	.HiHi.Cfg_	.HiHi.Cfg_	.HiHi.Cfg_	.Hi.Cfg_	.Hi.Cfg_	.Hi.Cfg_	.Hi.Cfg_	.HiGate.Cfg_	.HiGate.Cfg_	.HiGate.Cfg_	.HiGate.Cfg_	.HiGate.Cfg_	.Hi.Cfg_	.Hi.Cfg_	.Hi.Cfg_	.Hi.Cfg_	.Hi.Cfg_	.Hi.Cfg_	.Lo.Cfg_	.Lo.Cfg_	.Lo.Cfg_	.Lo.Cfg_	.LoGate.Cfg_	.LoGate.Cfg_	.LoGate.Cfg_	.LoGate.Cfg_	.LoGate.Cfg_	.Lo.Cfg_	.Lo.Cfg_	.Lo.Cfg_	.Lo.Cfg_	.Lo.Cfg_	.Lo.Cfg_	.LoLo.Cfg_	.LoLo.Cfg_	.LoLo.Cfg_	.LoLo.Cfg_	.LoLoGate.Cfg_	.LoLoGate.Cfg_	.LoLoGate.Cfg_	.LoLoGate.Cfg_	.LoLoGate.Cfg_	.LoLo.Cfg_	.LoLo.Cfg_	.LoLo.Cfg_	.LoLo.Cfg_	.LoLo.Cfg_	.LoLo.Cfg_	.Fail.Cfg_	.Fail.Cfg_	.Fail.Cfg_	.Fail.Cfg_	.FailGate.Cfg_	.FailGate.Cfg_	.FailGate.Cfg_	.FailGate.Cfg_	.FailGate.Cfg_	.Fail.Cfg_	.Fail.Cfg_	.Fail.Cfg_	.Fail.Cfg_	.Fail.Cfg_	.Fail.Cfg_	.Cfg_	.Cfg_
Unit	Tag Description	TagName	Instance	Desc	Label	Tag	Area	EU	HasHART	PVEUMin	PVEUMax	PVDecPlcs	FiltTC	HasPV	PVLabel	PVEU	HasSV	SVLabel	SVEU	SVDecPlcs	HasTV	TVLabel	TVEU	TVDecPlcs	HasFV	FVLabel	FVEU	FVDecPlcs	UseHARTText	UseHARTScaling	UseVarSts	AutoUpdDevInfo	ManUpdDevInfo	HasMoreObj	InpRawMin	InpRawMax	HiHiLim	HiHiDB	HiLim	HiDB	LoLim	LoDB	LoLoLim	LoLoDB	FailHiLim	FailLoLim	FailDB	NoSubstPV	Exists	ResetReqd	AckReqd	Severity	OnDly	OffDly	GateDly	InpCond	GateCond	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	OnDly	OffDly	GateDly	InpCond	GateCond	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	OnDly	OffDly	GateDly	InpCond	GateCond	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	OnDly	OffDly	GateDly	InpCond	GateCond	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	OnDly	OffDly	GateDly	InpCond	GateCond	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag	HasChanObj	UseChanSrcQ
		Default Values:	0	Analog Input (HART)	Analog Input	P_AInHART	area01	%	1	0.0	100.0	2	0.0	1			1			2	1			2	1			2	0	0	0	1	0	0	0.0	100.0	1.50E+38	1	1.50E+38	1	-1.50E+38	1	-1.50E+38	1	103.958336	-2.0833333	0.41666666	0	0	0	1	750	0	0	0	PV High-High	Gating Condition	1	1	5	480	High-High Alarm	XAHH-nnnn	0	0	1	500	0	0	0	PV High	Gating Condition	1	1	5	480	High Alarm	XAH-nnnn	0	0	1	500	0	0	0	PV Low	Gating Condition	1	1	5	480	Low Alarm	XAL-nnnn	0	0	1	750	0	0	0	PV Low-Low	Gating Condition	1	1	5	480	Low-Low Alarm	XALL-nnnn	0	0	1	1000	0	0	0	Input Failure	Gating Condition	1	1	5	480	Input Failure	XAF-nnnn	1	1
		PI_101	1	Analog Input (HART)	Analog Input	P_AInHART	area01	%	1	0.0	100.0	2	0.0	1			1			2	1			2	1			2	0	0	0	1	0	0	0.0	100.0	1.50000000274888E+038	1	1.50000000274888E+038	1	-1.50000000274888E+038	1	-1.50000000274888E+038	1	103.958336	-2.0833333	0.41666666	0	0	0	1	750	0	0	0	PV High-High	Gating Condition	1	1	5	480	High-High Alarm	XAHH-nnnn	0	0	1	500	0	0	0	PV High	Gating Condition	1	1	5	480	High Alarm	XAH-nnnn	0	0	1	500	0	0	0	PV Low	Gating Condition	1	1	5	480	Low Alarm	XAL-nnnn	0	0	1	750	0	0	0	PV Low-Low	Gating Condition	1	1	5	480	Low-Low Alarm	XALL-nnnn	0	0	1	1000	0	0	0	Input Failure	Gating Condition	1	1	5	480	Input Failure	XAF-nnnn	1	1
			2
			3
			4
			5
			6
			7
			8
			9
			10
			11
			12
			13
			14
			15
			16
			17
			18
			19
			20
			21
			22
			23
			24
			25
			26
			27
			28
			29	Strings too long to fit are formatted like this.
			30
			31
			32
			33
			34
			35
			36
			37
			38
			39
			40
			41
			42
			43
			44
			45
			46
			47
			48
			49
			50
			51
			52
			53
			54
			55
			56
			57
			58
			59
			60
			61
			62
			63
			64
			65
			66
			67
			68
			69
			70
			71
			72
			73
			74
			75
			76
			77
			78
			79
			80
			81
			82
			83
			84
			85
			86
			87
			88
			89
			90
			91
			92
			93
			94
			95
			96
			97
			98
			99

## P_AInMulti
	P_AInMulti: Multiple (to 8) Analog Input	Read From CLX:
		Send To CLX:

		Description:		Description for display on HMI	Label for graphic symbol displayed on HMI	Tagname for display on HMI	Process Area for security	Engineering Units for display on HMI	Tagname for Sensor/ Input A for display on HMI	Tagname for Sensor/ Input B for display on HMI	Tagname for Sensor/ Input C for display on HMI	Tagname for Sensor/ Input D for display on HMI	Tagname for Sensor/ Input E for display on HMI	Tagname for Sensor/ Input F for display on HMI	Tagname for Sensor/ Input G for display on HMI	Tagname for Sensor/ Input H for display on HMI	1=Inp_PVA is connected in logic	1=Inp_PVB is connected in logic	1=Inp_PVC is connected in logic	1=Inp_PVD is connected in logic	1=Inp_PVE is connected in logic	1=Inp_PVF is connected in logic	1=Inp_PVG is connected in logic	1=Inp_PVH is connected in logic	1=Inp_PVA should be used in PV calc if good	1=Inp_PVB should be used in PV calc if good	1=Inp_PVC should be used in PV calc if good	1=Inp_PVD should be used in PV calc if good	1=Inp_PVE should be used in PV calc if good	1=Inp_PVF should be used in PV calc if good	1=Inp_PVG should be used in PV calc if good	1=Inp_PVH should be used in PV calc if good	Input (unscaled) Minimum for Scaling	Input (unscaled) Maximum for Scaling	PV (Output) Minimum for Scaling to EU	PV (Output) Maximum for Scaling to EU	1=Tells HMI an object with more info is available	Number of decimal places for PV display (0..6)	Absolute Deviation Threshold (in EU): reject ouside this dev. from mean	PV Filter Time Constant (sec), 0.0 = unfiltered	Min. Good inputs for good PV [1..number of "Cfg_Has" inputs]	PV Calculation when only 2 good inputs: 0=Average, 1=Minimum, 2=Maximum	1=Reject an Input if its quality is Uncertain	1=Reject outside 2 standard deviations; 0=Reject ouside Cfg_AbsDev from mean	1=Calculate Average of good inputs; 0=calculate Median of good inputs	1=Disallow selection of Substitute PV	1=Tells HMI a Channel object (AlChan, etc.) is used for Inp_PVA	1=Tells HMI a Channel object (AlChan, etc.) is used for Inp_PVB	1=Tells HMI a Channel object (AlChan, etc.) is used for Inp_PVC	1=Tells HMI a Channel object (AlChan, etc.) is used for Inp_PVD	1=Tells HMI a Channel object (AlChan, etc.) is used for Inp_PVE	1=Tells HMI a Channel object (AlChan, etc.) is used for Inp_PVF	1=Tells HMI a Channel object (AlChan, etc.) is used for Inp_PVG	1=Tells HMI a Channel object (AlChan, etc.) is used for Inp_PVH	1=Pass thru connected Channel A's SrcQ value, 0=generate SrcQ	1=Pass thru connected Channel B's SrcQ value, 0=generate SrcQ	1=Pass thru connected Channel C's SrcQ value, 0=generate SrcQ	1=Pass thru connected Channel D's SrcQ value, 0=generate SrcQ	1=Pass thru connected Channel E's SrcQ value, 0=generate SrcQ	1=Pass thru connected Channel F's SrcQ value, 0=generate SrcQ	1=Pass thru connected Channel G's SrcQ value, 0=generate SrcQ	1=Pass thru connected Channel H's SrcQ value, 0=generate SrcQ	High-High Alarm Condition	High-High Alarm Tag	1=High-High Alarm exists and will be checked	1=Reset required to clear High-High Alarm	1=Acknowledge required for High-High Alarm	High-High Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	High Status Threshold	High Status Deadband (EU)	High Status Input Condition	High Status Gate Condition	High Status Gate Delay (s)	Minimum time above High Limit to raise Status (sec)	Minimum time below High Limit (minus deadband) to clear Status (sec)	High Alarm Condition	High Alarm Tag	1=High Alarm exists and will be checked	1=Reset required to clear High Alarm	1=Acknowledge required for High Alarm	High Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	Low Status Threshold	Low Status Deadband (EU)	Low Status Input Condition	Low Status Gate Condition	Low Status Gate Delay (s)	Minimum time below Low Limit to raise Status (sec)	Minimum time above Low Limit (plus deadband) to clear Status (sec)	Low Alarm Condition	Low Alarm Tag	1=Low Alarm exists and will be checked	1=Reset required to clear Low Alarm	1=Acknlowledge required for Low Alarm	Low Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	Low-Low Status Threshold	Low-Low Status Deadband (EU)	Lo-Lo Status Input Condition	Lo-Lo Status Gate Condition	Low-Low Status Gate Delay (s)	Minimum time below Low-Low Limit to raise Status (sec)	Minimum time above Low-Low Limit (plus deadband) to clear Status (sec)	Low-Low Alarm Condition	Low-Low Alarm Tag	1=Low-Low Alarm exists and will be checked	1=Reset required to clear Low-Low Alarm	1=Acknowledge required for Low-Low Alarm	Low-Low Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	Any Input Rejected Alarm Condition	Any Input Rejected Alarm Tag	1=Any Input Rejected Alarm exists and will be checked	1=Reset required to clear Any Input Rejected Alarm	1=Acknowledge required for Any Input Rejected Alarm	Any Input Rejected Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved tOneGoods long (min)	Minimum Good Signals Alarm Condition	Minimum Good Signals Alarm Tag	1=Minimum Good Signals Alarm exists and will be checked	1=Reset required to clear Minimum Good Signals Alarm	1=Acknowledge required for Minimum Good Signals Alarm	Minimum Good Signals Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	Input Failure (fail) High Limit (RAW)	Input Failure (fail) Low Limit (RAW)	Input Failure (fail) High/Low Deadband (RAW)	Input Failure Status Input Condition	Input Failure Status Gate Condition	Input Failure Status Gate Delay (s)	Minimum time Bad or Out of Range to raise Fail Status (sec)	Minimum time OK or In Range to clear Fail Status (sec)	Fail Alarm Condition	Fail Alarm Tag	1=Analog Input Failure Alarm exists and will be checked	1=Reset required to clear Analog InputFailure Alarm	1=Acknowledge required for Analog Input Failure Alarm	Failure Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)
		Usage:		Local	Local	Local	Local	Local	Local	Local	Local	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Local	Local	Input	Input	Input	Input	Local	Local	Local	Local	Output	Input	Local	Local	Input	Input	Input	Local	Local	Input	Input	Input	Input	Local	Local	Local	Local	Input	Input	Local	Local	Input	Input	Input	Local	Local	Input	Input	Input	Input	Local	Local	Local	Local	Output	Input	Local	Local	Input	Input	Input	Local	Local	Input	Input	Input	Input	Local	Local	Local	Local	Local	Local	Input	Input	Input	Input	Local	Local	Local	Local	Local	Local	Input	Input	Input	Input	Local	Local	Local	Local	Input	Input	Input	Local	Local	Input	Input	Input	Local	Local	Input	Input	Input	Input	Local	Local	Local	Local
		Data Type:		STRING_40	STRING_20	STRING_20	STRING_Area	STRING_8	STRING_20	STRING_20	STRING_20	STRING_20	STRING_20	STRING_20	STRING_20	STRING_20	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	REAL	REAL	REAL	REAL	BOOL	DINT	REAL	REAL	DINT	DINT	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	REAL	REAL	STRING_20	STRING_20	REAL	REAL	REAL	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	REAL	REAL	STRING_20	STRING_20	REAL	REAL	REAL	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	REAL	REAL	STRING_20	STRING_20	REAL	REAL	REAL	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	REAL	REAL	REAL	STRING_20	STRING_20	REAL	REAL	REAL	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT
			(Origin)	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.HiHi.Cfg_	.HiHi.Cfg_	.HiHi.Cfg_	.HiHi.Cfg_	.HiHi.Cfg_	.HiHi.Cfg_	.HiHi.Cfg_	.HiHi.Cfg_	.Cfg_	.Cfg_	.HiGate.Cfg_	.HiGate.Cfg_	.HiGate.Cfg_	.HiGate.Cfg_	.HiGate.Cfg_	.Hi.Cfg_	.Hi.Cfg_	.Hi.Cfg_	.Hi.Cfg_	.Hi.Cfg_	.Hi.Cfg_	.Hi.Cfg_	.Hi.Cfg_	.Cfg_	.Cfg_	.LoGate.Cfg_	.LoGate.Cfg_	.LoGate.Cfg_	.LoGate.Cfg_	.LoGate.Cfg_	.Lo.Cfg_	.Lo.Cfg_	.Lo.Cfg_	.Lo.Cfg_	.Lo.Cfg_	.Lo.Cfg_	.Lo.Cfg_	.Lo.Cfg_	.Cfg_	.Cfg_	.LoLoGate.Cfg_	.LoLoGate.Cfg_	.LoLoGate.Cfg_	.LoLoGate.Cfg_	.LoLoGate.Cfg_	.LoLo.Cfg_	.LoLo.Cfg_	.LoLo.Cfg_	.LoLo.Cfg_	.LoLo.Cfg_	.LoLo.Cfg_	.LoLo.Cfg_	.LoLo.Cfg_	.AnyReject.Cfg_	.AnyReject.Cfg_	.AnyReject.Cfg_	.AnyReject.Cfg_	.AnyReject.Cfg_	.AnyReject.Cfg_	.AnyReject.Cfg_	.AnyReject.Cfg_	.MinGood.Cfg_	.MinGood.Cfg_	.MinGood.Cfg_	.MinGood.Cfg_	.MinGood.Cfg_	.MinGood.Cfg_	.MinGood.Cfg_	.MinGood.Cfg_	.Cfg_	.Cfg_	.Cfg_	.FailGate.Cfg_	.FailGate.Cfg_	.FailGate.Cfg_	.FailGate.Cfg_	.FailGate.Cfg_	.Fail.Cfg_	.Fail.Cfg_	.Fail.Cfg_	.Fail.Cfg_	.Fail.Cfg_	.Fail.Cfg_	.Fail.Cfg_	.Fail.Cfg_
Unit	Tag Description	TagName	Instance	Desc	Label	Tag	Area	EU	PVATag	PVBTag	PVCTag	PVDTag	PVETag	PVFTag	PVGTag	PVHTag	HasPVA	HasPVB	HasPVC	HasPVD	HasPVE	HasPVF	HasPVG	HasPVH	UsePVA	UsePVB	UsePVC	UsePVD	UsePVE	UsePVF	UsePVG	UsePVH	InpRawMin	InpRawMax	PVEUMin	PVEUMax	HasMoreObj	PVDecPlcs	AbsDevLim	FiltTC	MinGood	CalcWhen2	RejectUncertain	UseStdDev	CalcAvg	NoSubstPV	HasChanObjA	HasChanObjB	HasChanObjC	HasChanObjD	HasChanObjE	HasChanObjF	HasChanObjG	HasChanObjH	UseChanSrcQA	UseChanSrcQB	UseChanSrcQC	UseChanSrcQD	UseChanSrcQE	UseChanSrcQF	UseChanSrcQG	UseChanSrcQH	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	HiLim	HiDB	InpCond	GateCond	GateDly	OnDly	OffDly	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	LoLim	LoDB	InpCond	GateCond	GateDly	OnDly	OffDly	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	LoLoLim	LoLoDB	InpCond	GateCond	GateDly	OnDly	OffDly	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	FailHiLim	FailLoLim	FailDB	InpCond	GateCond	GateDly	OnDly	OffDly	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT
		Default Values:	0	Multiple (to 8) Analog Input	Analog Input	P_AInMulti	area01	%	Sensor / Input A	Sensor / Input B	Sensor / Input C	Sensor / Input D	Sensor / Input E	Sensor / Input F	Sensor / Input G	Sensor / Input H	1	1	1	0	0	0	0	0	1	1	1	0	0	0	0	0	0.0	100.0	0.0	100.0	0	2	10.0	0.0	2	0	0	0	0	0	0	0	0	0	0	0	0	0	PV High-High Alarm	P_AInMulti.HiHi	0	0	1	750	1	1	5	480	1.5E+038	1	PV High Status	High Status Gate	0	0	0	PV High Alarm	P_AInMulti.Hi	0	0	1	500	1	1	5	480	-1.5E+038	1.0	PV Low Status	Low Status Gate	0	0	0	PV Low Alarm	P_AInMulti.Lo	0	0	1	500	1	1	5	480	-1.5E+038	1.0	PV Lo-Lo Status	Lo-Lo Status Gate	0	0	0	PV Low-Low Alarm	P_AInMulti.LoLo	0	0	1	750	1	1	5	480	Any Input Rejected	P_AInMulti.AnyReject	0	0	1	500	1	1	5	480	Min Good Inputs	P_AInMulti.MinGood	0	0	1	500	1	1	5	480	103.958336	-2.0833333	0.41666666	Input Failure Status	Fail Status Gate	0	0	0	Input Failure Alarm	P_AInMulti.Fail	0	0	1	1000	1	1	5	480
		MyP_AInMulti	1	Multiple (to 8) Analog Input	Analog Input	P_AInMulti	area01	%	Sensor / Input A	Sensor / Input B	Sensor / Input C	Sensor / Input D	Sensor / Input E	Sensor / Input F	Sensor / Input G	Sensor / Input H	1	1	1	0	0	0	0	0	1	1	1	0	0	0	0	0	0	100	0	100	0	2	10	0	2	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	PV High-High Alarm	P_AInMulti.HiHi	0	0	1	750	1	1	5	480	1.50000000274888E+038	1	PV High Status	High Status Gate	0	0	0	PV High Alarm	P_AInMulti.Hi	0	0	1	500	1	1	5	480	-1.50000000274888E+038	1	PV Low Status	Low Status Gate	0	0	0	PV Low Alarm	P_AInMulti.Lo	0	0	1	500	1	1	5	480	-1.50000000274888E+038	1	PV Lo-Lo Status	Lo-Lo Status Gate	0	0	0	PV Low-Low Alarm	P_AInMulti.LoLo	0	0	1	750	1	1	5	480	Any Input Rejected	P_AInMulti.AnyReject	0	0	1	500	1	1	5	480	Min Good Inputs	P_AInMulti.MinGood	0	0	1	500	1	1	5	480	103.958335876465	-2.08333325386047	0.416666656732559	Input Failure Status	Fail Status Gate	0	0	0	PV Input Failure	P_AInMulti.Fail	0	0	1	1000	1	1	5	480
			2
			3
			4
			5
			6
			7
			8
			9
			10
			11
			12
			13
			14
			15
			16
			17
			18
			19
			20
			21
			22
			23
			24
			25
			26
			27
			28
			29
			30	Strings too long to fit are formatted like this.
			31
			32
			33
			34
			35
			36
			37
			38
			39
			40
			41
			42
			43
			44
			45
			46
			47
			48
			49
			50
			51
			52
			53
			54
			55
			56
			57
			58
			59
			60
			61
			62
			63
			64
			65
			66
			67
			68
			69
			70
			71
			72
			73
			74
			75
			76
			77
			78
			79
			80
			81
			82
			83
			84
			85
			86
			87
			88
			89
			90
			91
			92
			93
			94
			95
			96
			97
			98
			99

## P_AInPAR
	P_AInPAR: Analog Input from ProfiBus PA	Read From CLX:
	via 1788-EN2PAR / B or 1788hp-EN2PA-R / A	Send To CLX:

		Description:		Description for display on HMI	Label for graphic symbol displayed on HMI	Tagname for display on HMI	Process Area for security	Engineering Units for display on HMI	Select PV to use for this AIn (1..8)	PV (Output) Minimum for Scaling to EU	PV (Output) Maximum for Scaling to EU	Number of decimal places for PV display (0..6)	PV Filter Time Constant (sec), 0.0 = unfiltered	1=Tells HMI an object with more info is available	High-High Status Threshold (EU)	High-High Status Deadband (EU)	High Status Threshold (EU)	High Status Deadband (EU)	Low Status Threshold (EU)	Low Status Deadband (EU)	Low-Low Status Threshold (EU)	Low-Low Status Deadband (EU)	Out-of-Range (fail) High Limit (EU)	Out-of-Range (fail) Low Limit (EU)	Out-of-Range (fail) High/Low Deadband (EU)	1=Disallow selection of Substitute PV	1=High-High Alarm exists and will be checked	1=Reset required to clear High-High Alarm	1=Acknowledge required for High-High Alarm	High-High Alarm Severity 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	Minimum time above High-High Limit to raise Status (s)	Minimum time below High-High Limit (minus deadband) to clear Status (s)	High-High Status Gate Delay (s)	High-High Status Input Condition	High-High Status Gate Condition	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	High-High Alarm Condition	High-High Alarm Tag	1=High Alarm exists and will be checked	1=Reset required to clear High Alarm	1=Acknowledge required for High Alarm	High Alarm Severity 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	Minimum time above High Limit to raise Status (s)	Minimum time below High Limit (minus deadband) to clear Status (s)	High Status Gate Delay (s)	High Status Input Condition	High Status Gate Condition	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	High Alarm Condition	High Alarm Tag	1=Low Alarm exists and will be checked	1=Reset required to clear Low Alarm	1=Acknlowledge required for Low Alarm	Low Alarm Severity 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	Minimum time below Low Limit to raise Status (s)	Minimum time above Low Limit (plus deadband) to clear Status (s)	Low Status Gate Delay (s)	Low Status Input Condition	Low Status Gate Condition	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	Low Alarm Condition	Low Alarm Tag	1=Low-Low Alarm exists and will be checked	1=Reset required to clear Low-Low Alarm	1=Acknowledge required for Low-Low Alarm	Low-Low Alarm Severity 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	Minimum time below Low-Low Limit to raise Status (s)	Minimum time above Low-Low Limit (plus deadband) to clear Status (s)	Low-Low Status Gate Delay (s)	Lo-Lo Status Input Condition	Lo-Lo Status Gate Condition	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	Low-Low Alarm Condition	Low-Low Alarm Tag	1=Analog Input Failure Alarm exists and will be checked	1=Reset required to clear Analog InputFailure Alarm	1=Acknowledge required for Analog Input Failure Alarm	Failure Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	Minimum time Bad or Out of Range to raise Fail Status (s)	Minimum time OK or In Range to clear Fail Status (s)	Fail Status Gate Delay (s)	Fail Status Input Condition	Fail Status Gate Condition	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	Fail Alarm Condition	Fail Alarm Tag
		Usage:		Local	Local	Local	Local	Local	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Local	Local	Local	Local	Local	Local	Local	Local	Input	Input	Input	Input	Input	Input	Input	Local	Local	Local	Local	Local	Local	Local	Local	Input	Input	Input	Input	Input	Input	Input	Local	Local	Local	Local	Local	Local	Local	Local	Input	Input	Input	Input	Input	Input	Input	Local	Local	Local	Local	Local	Local	Local	Local	Input	Input	Input	Input	Input	Input	Input	Local	Local	Local	Local	Local	Local	Local	Local
		Data Type:		STRING_40	STRING_20	STRING_20	STRING_Area	STRING_8	DINT	REAL	REAL	DINT	REAL	BOOL	REAL	REAL	REAL	REAL	REAL	REAL	REAL	REAL	REAL	REAL	REAL	BOOL	BOOL	BOOL	BOOL	DINT	REAL	REAL	REAL	STRING_20	STRING_20	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	REAL	REAL	REAL	STRING_20	STRING_20	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	REAL	REAL	REAL	STRING_20	STRING_20	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	REAL	REAL	REAL	STRING_20	STRING_20	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	REAL	REAL	REAL	STRING_20	STRING_20	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20
			(Origin)	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.HiHi.Cfg_	.HiHi.Cfg_	.HiHi.Cfg_	.HiHi.Cfg_	.HiHiGate.Cfg_	.HiHiGate.Cfg_	.HiHiGate.Cfg_	.HiHiGate.Cfg_	.HiHiGate.Cfg_	.HiHi.Cfg_	.HiHi.Cfg_	.HiHi.Cfg_	.HiHi.Cfg_	.HiHi.Cfg_	.HiHi.Cfg_	.Hi.Cfg_	.Hi.Cfg_	.Hi.Cfg_	.Hi.Cfg_	.HiGate.Cfg_	.HiGate.Cfg_	.HiGate.Cfg_	.HiGate.Cfg_	.HiGate.Cfg_	.Hi.Cfg_	.Hi.Cfg_	.Hi.Cfg_	.Hi.Cfg_	.Hi.Cfg_	.Hi.Cfg_	.Lo.Cfg_	.Lo.Cfg_	.Lo.Cfg_	.Lo.Cfg_	.LoGate.Cfg_	.LoGate.Cfg_	.LoGate.Cfg_	.LoGate.Cfg_	.LoGate.Cfg_	.Lo.Cfg_	.Lo.Cfg_	.Lo.Cfg_	.Lo.Cfg_	.Lo.Cfg_	.Lo.Cfg_	.LoLo.Cfg_	.LoLo.Cfg_	.LoLo.Cfg_	.LoLo.Cfg_	.LoLoGate.Cfg_	.LoLoGate.Cfg_	.LoLoGate.Cfg_	.LoLoGate.Cfg_	.LoLoGate.Cfg_	.LoLo.Cfg_	.LoLo.Cfg_	.LoLo.Cfg_	.LoLo.Cfg_	.LoLo.Cfg_	.LoLo.Cfg_	.Fail.Cfg_	.Fail.Cfg_	.Fail.Cfg_	.Fail.Cfg_	.FailGate.Cfg_	.FailGate.Cfg_	.FailGate.Cfg_	.FailGate.Cfg_	.FailGate.Cfg_	.Fail.Cfg_	.Fail.Cfg_	.Fail.Cfg_	.Fail.Cfg_	.Fail.Cfg_	.Fail.Cfg_
Unit	Tag Description	TagName	Instance	Desc	Label	Tag	Area	EU	PVSelect	PVEUMin	PVEUMax	PVDecPlcs	FiltTC	HasMoreObj	HiHiLim	HiHiDB	HiLim	HiDB	LoLim	LoDB	LoLoLim	LoLoDB	FailHiLim	FailLoLim	FailDB	NoSubstPV	Exists	ResetReqd	AckReqd	Severity	OnDly	OffDly	GateDly	InpCond	GateCond	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	OnDly	OffDly	GateDly	InpCond	GateCond	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	OnDly	OffDly	GateDly	InpCond	GateCond	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	OnDly	OffDly	GateDly	InpCond	GateCond	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	OnDly	OffDly	GateDly	InpCond	GateCond	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag
		Default Values:	0	Analog Input (Profibus PA)	Analog Input (PA)	P_AInPAR	area01	%	1	0.0	100.0	2	0.0	0	1.50E+38	1	1.50E+38	1	-1.50E+38	1	-1.50E+38	1	103.958336	-2.0833333	0.41666666	0	0	0	1	750	0	0	0	PV High-High	Gating Condition	1	1	5	480	High-High Alarm	XAHH-nnnn	0	0	1	500	0	0	0	PV High	Gating Condition	1	1	5	480	High Alarm	XAH-nnnn	0	0	1	500	0	0	0	PV Low	Gating Condition	1	1	5	480	Low Alarm	XAL-nnnn	0	0	1	750	0	0	0	PV Low-Low	Gating Condition	1	1	5	480	Low-Low Alarm	XALL-nnnn	0	0	1	1000	0	0	0	Input Failure	Gating Condition	1	1	5	480	Input Failure	XAF-nnnn
		MyP_AInPAR	1	Analog Input (Profibus PA)	Analog Input (PA)	P_AInPAR	area01	%	1	0	100	2	0	0	1.50000000274888E+038	1	1.50000000274888E+038	1	-1.50000000274888E+038	1	-1.50000000274888E+038	1	103.958335876465	-2.08333325386047	0.416666656732559	0	1	0	1	750	0	0	0	PV High-High	Gating Condition	1	1	5	480	High-High Alarm	XAHH-nnnn	1	0	1	500	0	0	0	PV High	Gating Condition	1	1	5	480	High Alarm	XAH-nnnn	1	0	1	500	0	0	0	PV Low	Gating Condition	1	1	5	480	Low Alarm	XAL-nnnn	1	0	1	750	0	0	0	PV Low-Low	Gating Condition	1	1	5	480	Low-Low Alarm	XALL-nnnn	1	0	1	1000	0	0	0	Input Failure	Gating Condition	1	1	5	480	Input Failure	XAF-nnnn
			2
			3
			4
			5
			6
			7
			8
			9
			10
			11
			12
			13
			14
			15
			16
			17
			18
			19
			20
			21
			22
			23
			24
			25
			26
			27
			28
			29	Strings too long to fit are formatted like this.
			30
			31
			32
			33
			34
			35
			36
			37
			38
			39
			40
			41
			42
			43
			44
			45
			46
			47
			48
			49
			50
			51
			52
			53
			54
			55
			56
			57
			58
			59
			60
			61
			62
			63
			64
			65
			66
			67
			68
			69
			70
			71
			72
			73
			74
			75
			76
			77
			78
			79
			80
			81
			82
			83
			84
			85
			86
			87
			88
			89
			90
			91
			92
			93
			94
			95
			96
			97
			98
			99

## P_AOut
	P_AOut: Analog Output	Read From CLX:
		Send To CLX:

		Description:		Description for display on HMI	Label for graphic symbol displayed on HMI	Tagname for display on HMI	Process Area for security	Engineering Units for display on HMI	CV Minimum in Engineering Units (for scaling)	CV Maximum in Engineering Units (for scaling)	CV Minimum in I/O (raw) Units (for scaling)	CV Maximum in I/O (raw) Units (for scaling)	1=Tells HMI an object with more info is available	Number of decimal places for CV display (0..6)	Minimum CV (in EU, for limiting)	Maximum CV (in EU, for limiting)	CV Rate of Change Limit, Increasing, (EU/sec, 0=unlimited)	CV Rate of Change Limit, Decreasing, (EU/sec, 0=unlimited)	1=Skip RoC Limiting in Intlk, Maint, Ovrd modes	When Val_CVOut is greater than this value (in CV EU) set Sts_Active (for HMI)	1=Hold Output on Interlock, 0=Go to Cfg_IntlkCV	1=Stop Motor and Alarm on I/O Fault; 0=Alarm only on I/O Fault	CV Target when interlocked (if not Cfg_ShedHold)	1=Tells HMI a P_Intlk is connected to Inp_Intlk	1=Tells HMI to enable navigation to a connected CV object	Tagname for destination of CV Navigation button	Interlock Tripped Alarm Condition	Interlock Tripped Alarm Tag	1=Interlock Tripped Alarm exists and will be checked	1=Interlock Tripped Alarm is latched in, requires Reset Command to clear	1=Interlock Tripped Alarm must be acknowledged	Interlock Tripped Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	I/O Fault Alarm Condition	I/O Fault Alarm Tag	1=I/O Fault Alarm exists and will be checked	1=Reset required to clear I/O Fault Alarm	1=Acknowledge required for I/O Fault Alarm	I/O Fault Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	1=PSets track OSets in Oper, OSets track PSets in Prog, 0=no tracking	1=Prog/Oper Settings track Override/Hand CV	1=Override ignores Bypassable Intlk; 0=always use Intlk	1=Operator (unlocked) exists, can be selected	1=Operator Locked exists, can be selected	1=Program (unlocked) exists, can be selected	1=Program Locked exists, can be selected	1=External exists, can be selected	1=Maintenance exists, can be selected	1=Maintenance Out of Service exists, can be selected	1=Override supersedes Prog/Oper Lock, 0=don't override Lock	1=External supersedes Prog/Oper Lock, 0=don't override Lock	1=Power Up to Prog, 0=Power Up to Oper	Normal Source: 1=Program if no requests; 0=Operator if no requests	Command Priority: 1=Program Cmds Win; 0=Operator Cmds Win	1=PCmd_Prog used as a Level (1=Prog, 0=Oper)	1=PCmd_Lock used as a Level (1=Lock, 0=Unlock)	1=XCmd_Acq used as Level (1=Acq, 0=Rel)
		Usage:		Local	Local	Local	Local	Local	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Local	Local	Local	Input	Input	Input	Input	Local	Local	Local	Local	Local	Local	Input	Input	Input	Input	Local	Local	Local	Local	Input	Input	Input	Input	Input	Input	Input	Input
		Data Type:		STRING_40	STRING_20	STRING_20	STRING_Area	STRING_8	REAL	REAL	REAL	REAL	BOOL	DINT	REAL	REAL	REAL	REAL	BOOL	REAL	BOOL	BOOL	REAL	BOOL	BOOL	STRING_NavTag	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL
			(Origin)	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.Cfg_	.Cfg_	.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_
Unit	Tag Description	TagName	Instance	Desc	Label	Tag	Area	EU	CVEUMin	CVEUMax	CVRawMin	CVRawMax	HasMoreObj	DecPlcs	MinCV	MaxCV	CVRoCLimInc	CVRoCLimDec	SkipRoCLim	MaxInactiveCV	ShedHold	ShedOnIOFault	IntlkCV	HasIntlkObj	HasCVNav	CVNavTag	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	SetTrack	SetTrackOvrdHand	OvrdIntlk	HasOper	HasOperLocked	HasProg	HasProgLocked	HasExt	HasMaint	HasMOoS	OvrdOverLock	ExtOverLock	ProgPwrUp	ProgNormal	PCmdPriority	PCmdProgAsLevel	PCmdLockAsLevel	ExtAcqAsLevel
		Default Values:	0	Analog Output	Analog Output	P_AOut	area01	%	0.0	100.0	0.0	100.0	0	2	0.0	100.0	0	0	0	0.0	0	1	0.0	0	0		Interlock Trip	P_AOut.IntlkTrip	0	0	1	500	0	1	5	480	I/O Fault	P_AOut.IOFault	0	0	1	1000	0	1	5	480	1	0	0	1	1	1	1	0	1	1	1	0	0	0	0	0	0	0
		MyP_AOut	1	Analog Output	Analog Output	MyAOut	area01	%	0	100	0	100	0	2	0	100	0	0	0	0	0	1	0	1	0		Interlock Trip	MyAOut.IntlkTrip	1	0	1	3	1	1	5	480	I/O Fault	MyAOut.IOFault	1	0	1	3	1	1	5	480	1	0	0	1	1	1	1	0	1	1	1	0	0	0	0	0	0	0
			2
			3
			4
			5
			6
			7
			8
			9
			10
			11
			12
			13
			14
			15
			16
			17
			18
			19
			20
			21
			22
			23
			24
			25
			26
			27
			28
			29
			30	Strings too long to fit are formatted like this.
			31
			32
			33
			34
			35
			36
			37
			38
			39
			40
			41
			42
			43
			44
			45
			46
			47
			48
			49
			50
			51
			52
			53
			54
			55
			56
			57
			58
			59
			60
			61
			62
			63
			64
			65
			66
			67
			68
			69
			70
			71
			72
			73
			74
			75
			76
			77
			78
			79
			80
			81
			82
			83
			84
			85
			86
			87
			88
			89
			90
			91
			92
			93
			94
			95
			96
			97
			98
			99

## P_AOutHART
	P_AOutHART: HART Analog Output	Read From CLX:
	(Channel object)	Send To CLX:

		Description:		Description for display on HMI	Label for graphic symbol displayed on HMI	Tagname for display on HMI	Process Area for security	Engineering Units for CV display on HMI	Tagname for destination of CV Navigation button	Engineering Units for HART PV display on HMI	Label for Primary Variable for display on HMI	Engineering Units for HART SV display on HMI	Label for Secondary Variable for display on HMI	Engineering Units for HART TV display on HMI	Label for Third Variable for display on HMI	Engineering Units for HART FV display on HMI	Label for Fourth Variable for display on HMI	Minimum CV (in EU, for limiting)	Maximum CV (in EU, for limiting)	CV Target when interlocked (if not Cfg_ShedHold)	CV Minimum in Engineering Units (for scaling)	CV Maximum in Engineering Units (for scaling)	CV Minimum in I/O (raw) Units (for scaling)	CV Maximum in I/O (raw) Units (for scaling)	When Val_CVOut is greater than this value (in CV EU) set Sts_Active (for HMI)	1=Hold Output on Interlock, 0=Go to Cfg_IntlkCV	1=Skip RoC Limiting in Intlk, Maint, Ovrd modes	1=HART instrument, 0=non-HART (4-20 mA only) instrument	1=Digital PV (primary variable) is configured	1=Digital SV (secondary variable) is configured	1=Digital TV (third variable) is configured	1=Digital FV (fourth variable) is configured	1=Use HART text for Desc, Label, Tag, EU; 0=Manually entered	1=Use HART scaling for raw, EU ranges; 0=Manually entered ranges	1=automatically update device info, 0=no auto update	1=allow manual device info update request, 0=disallow	1=Tells HMI a P_Intlk is connected to Inp_Intlk	1=Tells HMI an object with more info is available	1=Tells HMI to enable navigation to a connected CV object	1=Stop Motor and Alarm on I/O Fault; 0=Alarm only on I/O Fault	Interlock Tripped Alarm Condition	Interlock Tripped Alarm Tag	1=Interlock Tripped Alarm exists and will be checked	1=Reset required to clear Interlock Trip Alarm	1=Acknowledged required for Interlock Trip Alarm	Interlock Tripped Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	I/O Fault Alarm Condition	I/O Fault Alarm Tag	1=I/O Fault Alarm exists and will be checked	1=Reset required to clear I/O Fault Alarm	1=Acknowledged required for I/O Fault Alarm	I/O Fault Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	1=PSets track OSets in Oper, OSets track PSets in Prog, 0=no tracking	1=Prog/Oper Settings track Override/Hand CV	1=Override ignores Bypassable Intlk; 0=always use Intlk	1=Operator (unlocked) exists, can be selected	1=Operator Locked exists, can be selected	1=Program (unlocked) exists, can be selected	1=Program Locked exists, can be selected	1=External exists, can be selected	1=Maintenance exists, can be selected	1=Maintenance Out of Service exists, can be selected	1=Override supersedes Prog/Oper Lock, 0=dont override Lock	1=External supersedes Prog/Oper Lock, 0=dont override Lock	1=Power Up to Prog, 0=Power Up to Oper	Normal Source: 1=Program if no requests; 0=Operator if no requests	Command Priority: 1=Program Cmds Win; 0=Operator Cmds Win	1=PCmd_Prog used as a Level (1=Prog, 0=Oper)	1=PCmd_Lock used as a Level (1=Lock, 0=Unlock)	1=XCmd_Acq used as Level (1=Acq, 0=Rel)
		Usage:		Local	Local	Local	Local	Local	Local	Local	Local	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Local	Local	Input	Input	Input	Input	Local	Local	Local	Local	Local	Local	Input	Input	Input	Input	Local	Local	Local	Local	Input	Input	Input	Input	Input	Input	Input	Input
		Data Type:		STRING_40	STRING_20	STRING_20	STRING_Area	STRING_8	STRING_NavTag	STRING_8	STRING_16	STRING_8	STRING_16	STRING_8	STRING_16	STRING_8	STRING_16	REAL	REAL	REAL	REAL	REAL	REAL	REAL	REAL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL
			(Origin)	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.Cfg_	.Cfg_	.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_
Unit	Tag Description	TagName	Instance	Desc	Label	Tag	Area	EU	CVNavTag	PVEU	PVLabel	SVEU	SVLabel	TVEU	TVLabel	FVEU	FVLabel	MinCV	MaxCV	IntlkCV	CVEUMin	CVEUMax	CVRawMin	CVRawMax	MaxInactiveCV	ShedHold	SkipRoCLim	HasHART	HasPV	HasSV	HasTV	HasFV	UseHARTText	UseHARTScaling	AutoUpdDevInfo	ManUpdDevInfo	HasIntlkObj	HasMoreObj	HasCVNav	ShedOnIOFault	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	SetTrack	SetTrackOvrdHand	OvrdIntlk	HasOper	HasOperLocked	HasProg	HasProgLocked	HasExt	HasMaint	HasMOoS	OvrdOverLock	ExtOverLock	ProgPwrUp	ProgNormal	PCmdPriority	PCmdProgAsLevel	PCmdLockAsLevel	ExtAcqAsLevel
		Default Values:	0	Analog Output	Analog Output	P_AOutHART	area01	%					0.0	100.0	0.0	0.0	100.0	0.0	100.0	0.0	0	0	1	1	1	1	1	0	0	1	0	0	0	0	1	Interlock Trip	P_AOut.IntlkTrip	0	0	1	500	0	1	5	480	I/O Fault	P_AOut.IOFault	0	0	1	1000	0	1	5	480	1	0	0	1	1	1	1	0	1	1	1	0	0	0	0	0	0	0
		PV_101	1	Analog Output (HART)	1734sc-OE2CIH		area01	%					0	100	0	0	0	4000	20000	0	0	0	1	1	1	1	1	0	1	1	1	0	0	0	1	Interlock Tripped	XAS-nnnn	0	0	1	500	1	1	5	0	I/O Fault	XAF-nnnn	0	0	1	1000	1	1	5	0	1	0	0	1	1	1	1	0	1	1	1	0	0	0	0	0	0	0
			2
			3
			4
			5
			6
			7
			8
			9
			10
			11
			12
			13
			14
			15
			16
			17
			18
			19
			20
			21
			22
			23
			24
			25
			26
			27
			28
			29	Strings too long to fit are formatted like this.
			30
			31
			32
			33
			34
			35
			36
			37
			38
			39
			40
			41
			42
			43
			44
			45
			46
			47
			48
			49
			50
			51
			52
			53
			54
			55
			56
			57
			58
			59
			60
			61
			62
			63
			64
			65
			66
			67
			68
			69
			70
			71
			72
			73
			74
			75
			76
			77
			78
			79
			80
			81
			82
			83
			84
			85
			86
			87
			88
			89
			90
			91
			92
			93
			94
			95
			96
			97
			98
			99

## P_D4SD
	P_D4SD: Discrete 2, 3 or 4 State Device	Read From CLX:
		Send To CLX:

		Description:		Description for display on HMI	Label for graphic symbol displayed on HMI	Tagname for display on HMI	Process Area for security	Text to display in State 0	Text to display in State 1	Text to display in State 2	Text to display in State 3	Number of device states (2..4)	1=OCmd_St0 has priority, accepted any time, 0=OCmd_St0 only in Oper, Maint Mode.	1=XCmd_St0 any time, 0=XCmd_St0 only when Ext selected	Bit=1: write output in state 0, Bit=0: leave in last state	(if written) Bit=1: output set in State 0, Bit=0: output cleared	Bit=1: write output in state 1, Bit=0: leave in last state	(if written) Bit=1: output set in State 1, Bit=0: output cleared	Bit=1: write output in state 2, Bit=0: leave in last state	(if written) Bit=1: output set in State 2, Bit=0: output cleared	Bit=1: write output in state 3, Bit=0: leave in last state	(if written) Bit=1: output set in State 3, Bit=0: output cleared	Time to pulse Output A (sec) (0=output held continuously)	Time to pulse Output B (sec) (0=output held continuously)	Time to pulse Output C (sec) (0=output held continuously)	Time to pulse Output D (sec) (0=output held continuously)	Bit=1: Check Feedback in state 0, Bit=0: dont care	(if checking) Bit=1: Feedback is 1 in State 0, Bit=0: Feedback is 0	Bit=1: Check Feedback in state 1, Bit=0: dont care	(if checking) Bit=1: Feedback is 1 in State 1, Bit=0: Feedback is 0	Bit=1: Check Feedback in state 2, Bit=0: dont care	(if checking) Bit=1: Feedback is 1 in State 2, Bit=0: Feedback is 0	Bit=1: Check Feedback in state 3, Bit=0: dont care	(if checking) Bit=1: Feedback is 1 in State 3, Bit=0: Feedback is 0	Time after new state requested to reach that state before Fault (sec)	1=Go to State 0 on Shed, 0=Hold position on Shed	1=Go to State 0 and Alarm on Fail to reach position; 0=Alarm only on Fail	1=Go to State 0 and Alarm on Device Fault; 0=Alarm only on Device Fault	1=Go to State 0 and Alarm on I/O Fault; 0=Alarm only on I/O Fault	Delay to echo back reaching state when in Simulation (sec)	0 = Horn on energize only, 1 = Horn on any state change	Time to sound audible on commanded energize (sec) (0=disabled)	1=Tells HMI a P_Perm is connected to Inp_PermOK0	1=Tells HMI a P_Perm is connected to Inp_PermOK1	1=Tells HMI a P_Perm is connected to Inp_PermOK2	1=Tells HMI a P_Perm is connected to Inp_PermOK3	1=Tells HMI a P_Intlk is connected to Inp_IntlkOK	1=Tells HMI an object with more info is available	1=OCmd_St0 has priority, accepted any time, 0=OCmd_St0 only in Oper, Maint Mode.	Position Fail Alarm Tag	1=Position Fail Alarm exists and will be checked	1=Position Fail Alarm is latched in, requires Reset Command to clear	1=Position Fail Alarm must be acknowledged	Position Fail Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	Device Fault Alarm Condition	Device Fault Alarm Tag	1=Device Fault Alarm exists and will be checked	1=Device Fault Alarm is latched in, requires Reset Command to clear	1=Device Fault Alarm must be acknowledged	Device Fault Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	Interlock Tripped Alarm Condition	Interlock Tripped Alarm Tag	1=Interlock Tripped Alarm exists and will be checked	1=Interlock Tripped Alarm is latched in, requires Reset Command to clear	1=Interlock Tripped Alarm must be acknowledged	Interlock Tripped Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	I/O Fault Alarm Condition	I/O Fault Alarm Tag	1=I/O Fault Alarm exists and will be checked	1=Reset required to clear I/O Fault Alarm	1=Acknowledge required for I/O Fault Alarm	I/O Fault Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	1=New device Ocmd resets shed latches and cleared alarms, 0=OCmdReset reqd	1=New Device XCmd resets shed latches and cleared alarms, 0=XCmdReset reqd	1=Override ignores Bypassable Perm/ Intlk; 0=always use Perm/Intlk	1=Operator (unlocked) exists, can be selected	1=Operator Locked exists, can be selected	1=Program (unlocked) exists, can be selected	1=Program Locked exists, can be selected	1=External exists, can be selected	1=Maintenance exists, can be selected	1=Maintenance Out of Service exists, can be selected	1=Override supersedes Prog/Oper Lock, 0=don't override Lock	1=External supersedes Prog/Oper Lock, 0=don't override Lock	1=Power Up to Prog, 0=Power Up to Oper	Normal Source: 1=Program if no requests; 0=Operator if no requests	Command Priority: 1=Program Cmds Win; 0=Operator Cmds Win	1=PCmd_Prog used as a Level (1=Prog, 0=Oper)	1=PCmd_Lock used as a Level (1=Lock, 0=Unlock)	1=XCmd_Acq used as Level (1=Acq, 0=Rel)
		Usage:		Local	Local	Local	Local	Local	Local	Local	Local	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Local	Local	Input	Input	Input	Input	Local	Local	Local	Local	Local	Local	Input	Input	Input	Input	Local	Local	Local	Local	Local	Local	Input	Input	Input	Input	Local	Local	Local	Local	Local	Local	Input	Input	Input	Input	Local	Local	Local	Local	Input	Input	Input	Input	Input	Input	Input	Input
		Data Type:		STRING_40	STRING_20	STRING_20	STRING_Area	STRING_8	STRING_8	STRING_8	STRING_8	DINT	BOOL	BOOL	SINT	SINT	SINT	SINT	SINT	SINT	SINT	SINT	REAL	REAL	REAL	REAL	SINT	SINT	SINT	SINT	SINT	SINT	SINT	SINT	REAL	BOOL	BOOL	BOOL	BOOL	REAL	BOOL	REAL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL
			(Origin)	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Fail.Cfg_	.Fail.Cfg_	.Fail.Cfg_	.Fail.Cfg_	.Fail.Cfg_	.Fail.Cfg_	.Fail.Cfg_	.Fail.Cfg_	.DeviceFault.Cfg_	.DeviceFault.Cfg_	.DeviceFault.Cfg_	.DeviceFault.Cfg_	.DeviceFault.Cfg_	.DeviceFault.Cfg_	.DeviceFault.Cfg_	.DeviceFault.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.Cfg_	.Cfg_	.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_
Unit	Tag Description	TagName	Instance	Desc	Label	Tag	Area	St0Text	St1Text	St2Text	St3Text	NumStates	OperSt0Prio	ExtSt0Prio	OutSt0Write	OutSt0State	OutSt1Write	OutSt1State	OutSt2Write	OutSt2State	OutSt3Write	OutSt3State	OutAPulseT	OutBPulseT	OutCPulseT	OutDPulseT	FdbkSt0Check	FdbkSt0State	FdbkSt1Check	FdbkSt1State	FdbkSt2Check	FdbkSt2State	FdbkSt3Check	FdbkSt3State	FailT	St0onShed	ShedOnFail	ShedOnDeviceFault	ShedOnIOFault	SimFdbkT	HornOnChange	StartHornT	HasPerm0Obj	HasPerm1Obj	HasPerm2Obj	HasPerm3Obj	HasIntlkObj	HasMoreObj	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	OCmdResets	XCmdResets	OvrdPermIntlk	HasOper	HasOperLocked	HasProg	HasProgLocked	HasExt	HasMaint	HasMOoS	OvrdOverLock	ExtOverLock	ProgPwrUp	ProgNormal	PCmdPriority	PCmdProgAsLevel	PCmdLockAsLevel	ExtAcqAsLevel
		Default Values:	0	Discrete 2, 3 or 4 State Device	Discrete Device	P_D4SD	area01	Off	On			2	0	0	2#0000_1111	2#0000_0001	2#0000_1111	2#0000_0010	2#0000_1111	2#0000_0100	2#0000_1111	2#0000_1000	0.0	0.0	0.0	0.0	2#0000_0000	2#0000_0001	2#0000_0000	2#0000_0010	2#0000_0000	2#0000_0100	2#0000_0000	2#0000_1000	10	0	0	0	0	2	0	0	0	0	0	0	0	0	Position Fail	P_D4SD.Fail	0	0	1	1000	0	1	5	480	Device Fault	P_D4SD.DeviceFault	0	0	1	1000	0	1	5	480	Interlock Trip	P_D4SD.IntlkTrip	0	0	1	500	0	1	5	480	I/O Fault	P_D4SD.IOFault	0	0	1	1000	0	1	5	480	0	0	0	1	1	1	1	0	1	1	1	0	0	0	0	0	0	0
		MyP_D4SD	1	Discrete 2-, 3- or 4-State Device	Discrete Device	P_D4SD	area01	North	East	South	West	4	0	0	15	1	15	2	15	4	15	8	3	3	3	3	15	1	15	2	15	4	15	8	10	0	1	1	1	4	0	0	0	0	0	0	0	0	Position Failure	P_D4SD.Fail	1	0	1	3	1	1	5	480	Device Fault	P_D4SD.DeviceFault	1	0	1	3	1	1	5	480	Interlock Trip	P_D4SD.IntlkTrip	1	0	1	3	1	1	5	480	I/O Fault	P_D4SD.IOFault	1	0	1	3	1	1	5	480	0	0	0	1	1	1	1	0	1	1	1	0	0	0	0	0	0	0
			2
			3
			4
			5
			6
			7
			8
			9
			10
			11
			12
			13
			14
			15
			16
			17
			18
			19
			20
			21
			22
			23
			24
			25
			26
			27
			28
			29
			30	Strings too long to fit are formatted like this.
			31
			32
			33
			34
			35
			36
			37
			38
			39
			40
			41
			42
			43
			44
			45
			46
			47
			48
			49
			50
			51
			52
			53
			54
			55
			56
			57
			58
			59
			60
			61
			62
			63
			64
			65
			66
			67
			68
			69
			70
			71
			72
			73
			74
			75
			76
			77
			78
			79
			80
			81
			82
			83
			84
			85
			86
			87
			88
			89
			90
			91
			92
			93
			94
			95
			96
			97
			98
			99

## P_DBC
	P_DBC: Deadband Controller	Read From CLX:
		Send To CLX:

		Description:		Description for display on HMI	Label for graphic symbol displayed on HMI	Tagname for display on HMI	Process Area for security	Engineering Units for display on HMI	1=Tells HMI to enable navigation to a connected PV object	Tagname for destination of PV Navigation button	1=Tells HMI to enable navigation to a connected output object	Tagname for destination of Output Navigation button	PV (Input) Range Minimum (EU)	PV (Input) Range Maximum (EU)	1=Tells HMI an object with more info is available	Number of decimal places for PV display (0..6)	Setpoint High Limit (clamp) (EU)	Setpoint Low Limit (clamp) (EU)	Deadband for the Raise output (above Raise limit)	Deadband for the Lower output (below Lower limit)	PV Rate of Change time base (sec) 60=/min, 3600=/hr	High Deviation Status Threshold (EU)	High Deviation Status Deadband (EU)	Low Deviation Status Threshold (EU)	Low Deviation Status Deadband (EU)	Program-Entered High Rate of Change (Increasing) Status Threshold (EU/RateTime)	High Rate of Change (Increasing) Status Deadband (EU/RateTime)	Minimum time above High Rate of Change (Increasing) Limit to raise Status (sec)	Minimum time below High Rate of Change (Increasing) Limit (minus deadband) to clear Status (sec)	High Rate of Change (Increasing) Status Gate Delay (sec)	Program-Entered High Rate of Change (Decreasing) Status Threshold (EU/RateTime)	High Rate of Change (Decreasing) Status Deadband (EU/RateTime)	Minimum time above High Rate of Change (Decreasing) Limit to raise Status (sec)	Minimum time below High Rate of Change (Decreasing) Limit (minus deadband) to clear Status (sec)	High Rate of Change (Decreasing) Status Gate Delay (sec)	High Deviation Alarm Condition	High Deviation Alarm Tag	1=High Deviation Alarm exists and will be checked	1=High Deviation Alarm is latched in, requires Reset Command to clear	1=High Deviation Alarm must be acknowledged	High Deviation Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	Low Deviation Alarm Condition	Low Deviation Alarm Tag	1=Low Deviation Alarm exists and will be checked	1=Low Deviation Alarm is latched in, requires Reset Command to clear	1=Low Deviation Alarm must be acknowledged	Low Deviation Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	Hi Rate of Increaseped Alarm Condition	Hi Rate of Increaseped Alarm Tag	1=Hi Rate of Increaseped Alarm exists and will be checked	1=Hi Rate of Increaseped Alarm is latched in, requires Reset Command to clear	1=Hi Rate of Increaseped Alarm must be acknowledged	Hi Rate of Increaseped Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	Hi Rate of Decrease Alarm Condition	Hi Rate of Decrease Alarm Tag	1=Hi Rate of Decrease Alarm exists and will be checked	1=Hi Rate of Decrease Alarm is latched in, requires Reset Command to clear	1=Hi Rate of Decrease Alarm must be acknowledged	Hi Rate of Decrease Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	1=PSets track OSets in Oper, OSets track PSets in Prog, 0=no tracking	1=Operator (unlocked) exists, can be selected	1=Operator Locked exists, can be selected	1=Program (unlocked) exists, can be selected	1=Program Locked exists, can be selected	1=External exists, can be selected	1=Maintenance exists, can be selected	1=Maintenance Out of Service exists, can be selected	1=Override supersedes Prog/Oper Lock, 0=don't override Lock	1=External supersedes Prog/Oper Lock, 0=don't override Lock	1=Power Up to Prog, 0=Power Up to Oper	Normal Source: 1=Program if no requests; 0=Operator if no requests	Command Priority: 1=Program Cmds Win; 0=Operator Cmds Win	1=PCmd_Prog used as a Level (1=Prog, 0=Oper)	1=PCmd_Lock used as a Level (1=Lock, 0=Unlock)	1=XCmd_Acq used as Level (1=Acq, 0=Rel)
		Usage:		Local	Local	Local	Local	Local	Input	Local	Input	Local	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Local	Local	Local	Local	Local	Local	Local	Local	Input	Local	Local	Local	Local	Local	Local	Local	Local
		Data Type:		STRING_40	STRING_20	STRING_20	STRING_Area	STRING_8	BOOL	STRING_NavTag	BOOL	STRING_NavTag	REAL	REAL	BOOL	DINT	REAL	REAL	REAL	REAL	REAL	REAL	REAL	REAL	REAL	REAL	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL
			(Origin)	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.HiDev.Cfg_	.HiDev.Cfg_	.HiDev.Cfg_	.HiDev.Cfg_	.HiDev.Cfg_	.HiDev.Cfg_	.HiDev.Cfg_	.HiDev.Cfg_	.LoDev.Cfg_	.LoDev.Cfg_	.LoDev.Cfg_	.LoDev.Cfg_	.LoDev.Cfg_	.LoDev.Cfg_	.LoDev.Cfg_	.LoDev.Cfg_	.HiRoCInc.Cfg_	.HiRoCInc.Cfg_	.HiRoCInc.Cfg_	.HiRoCInc.Cfg_	.HiRoCInc.Cfg_	.HiRoCInc.Cfg_	.HiRoCInc.Cfg_	.HiRoCInc.Cfg_	.HiRoCDec.Cfg_	.HiRoCDec.Cfg_	.HiRoCDec.Cfg_	.HiRoCDec.Cfg_	.HiRoCDec.Cfg_	.HiRoCDec.Cfg_	.HiRoCDec.Cfg_	.HiRoCDec.Cfg_	.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_
Unit	Tag Description	TagName	Instance	Desc	Label	Tag	Area	PVEU	HasPVNav	PVNavTag	HasOutNav	OutNavTag	PVEUMin	PVEUMax	HasMoreObj	PVDecPlcs	SPHiLim	SPLoLim	RaiseDB	LowerDB	RateTime	HiDevLim	HiDevDB	LoDevLim	LoDevDB	HiRoCIncLim	HiRoCIncDB	HiRoCIncOnDly	HiRoCIncOffDly	HiRoCIncGateDly	HiRoCDecLim	HiRoCDecDB	HiRoCDecOnDly	HiRoCDecOffDly	HiRoCDecGateDly	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	SetTrack	HasOper	HasOperLocked	HasProg	HasProgLocked	HasExt	HasMaint	HasMOoS	OvrdOverLock	ExtOverLock	ProgPwrUp	ProgNormal	PCmdPriority	PCmdProgAsLevel	PCmdLockAsLevel	ExtAcqAsLevel
		Default Values:	0	Deadband Controller	On/Off Controller	P_DBC	area01	%	0		0		0	100	0	2	100	0	1.0	1.0	1.0	100	1	-100	1.0	100	1.0	1.0	1.0	1.0	100	1.0	1.0	1.0	1.0	High Deviation	XDAH-nnnn	0	0	1	1000	0	1	5	480	Low Deviation	XDAL-nnnn	0	0	1	1000	0	1	5	480	Hi Rate of Increase	XKAHR-nnnn	0	0	1	500	0	1	5	480	Hi Rate of Decrease	XKAHF-nnnn	0	0	1	1000	0	1	5	480	1	1	1	1	1	0	1	1	1	0	0	0	0	0	0	0
		MyP_DBC	1	Deadband Controller	On/Off Controller	P_DBC	area01	%	1		1		0	100	0	2	100	0	1	1	1	100	1	-100	1	100	1	0	0	0	100	1	0	0	0	Deviation High	P_DBC.HiDev	1	0	1	750	1	1	5	480	Deviation Low	P_DBC.LoDev	1	0	1	750	1	1	5	480	Hi Rate of Increase	XKAH-nnnnA	0	0	1	500	1	1	5	0	Hi Rate of Decrease	XKAH-nnnnB	0	0	1	500	1	1	5	0	0	1	1	1	1	0	1	1	1	0	0	0	0	0	0	0
			2
			3
			4
			5
			6
			7
			8
			9
			10
			11
			12
			13
			14
			15
			16
			17
			18
			19
			20
			21
			22
			23
			24
			25
			26
			27
			28
			29
			30
			31
			32
			33
			34
			35
			36
			37
			38
			39
			40
			41
			42
			43
			44
			45
			46
			47
			48
			49
			50
			51
			52
			53
			54
			55
			56
			57
			58
			59
			60
			61
			62
			63
			64
			65
			66
			67
			68
			69
			70
			71
			72
			73
			74
			75
			76
			77
			78
			79
			80
			81
			82
			83
			84
			85
			86
			87
			88
			89
			90
			91
			92
			93
			94
			95
			96
			97
			98
			99

## P_DIn
	P_DIn: Discrete Input	Read From CLX:
		Send To CLX:

		Description:		Description for display on HMI	Label for graphic symbol displayed on HMI	Tagname for display on HMI	Process Area for security	Text to display in PV=0 State	Text to display in PV=1 State	1=Disallow selection of Substitute PV	Minimum time Input Sts must maintain state (sec)	1=Display state text in "normal" state (= target), 0=hide (some HMI objects)	1=Tells HMI an object with more info is available	Target Disagree Status Input Condition	Target Disagree Status Gate Condition	Time Inp_Gate must be true before Disagree Status is checked (sec)	Minimum time for Input to disagree with Target to raise Status (sec)	Minimum time for Input to agree with Target to clear Status (sec)	Target Disagree Alarm Condition	Target Disagree Alarm Tag	1=Target Disagree Alarm exists and will be checked	1=Target Disagree Alarm is in latched in, requires Reset Command to clear	1=Target Disagree Alarm must be acknlowledge	Target Disagree Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	1=I/O Fault Alarm exists and will be checked	1=Reset required to clear I/O Fault Alarm	1=Acknowledge required for I/O Fault Alarm	I/O Fault Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)
		Usage:		Local	Local	Local	Local	Local	Local	Input	Input	Input	Input	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local
		Data Type:		STRING_40	STRING_20	STRING_20	STRING_Area	STRING_8	STRING_8	BOOL	REAL	BOOL	BOOL	STRING_20	STRING_20	REAL	REAL	REAL	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT
			(Origin)	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.TgtDisagreeGate.Cfg_	.TgtDisagreeGate.Cfg_	.TgtDisagreeGate.Cfg_	.TgtDisagreeGate.Cfg_	.TgtDisagreeGate.Cfg_	.TgtDisagree.Cfg_	.TgtDisagree.Cfg_	.TgtDisagree.Cfg_	.TgtDisagree.Cfg_	.TgtDisagree.Cfg_	.TgtDisagree.Cfg_	.TgtDisagree.Cfg_	.TgtDisagree.Cfg_	.TgtDisagree.Cfg_	.TgtDisagree.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_
Unit	Tag Description	TagName	Instance	Desc	Label	Tag	Area	0StText	1StText	NoSubstPV	Debounce	NormTextVis	HasMoreObj	InpCond	GateCond	GateDly	OnDly	OffDly	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT
		Default Values:	0	Discrete Input	Discrete Input	P_DIn	area01	Off	On	0	0	1	0	Target Disagree	Gating Condition	0	0	0	Target Disagree	XA-nnnn	0	0	1	750	1	1	5	480	0	0	1	1000	0	1	5	480
			1	None	None	None	None	None	None	None	None	None	None	None	None	None	None	None	None	None	None	None	None	None	None	None	None	None	None	None	None	None	None	None	None	None
			2
			3
			4
			5
			6
			7
			8
			9
			10
			11
			12
			13
			14
			15
			16
			17
			18
			19
			20
			21
			22
			23
			24
			25
			26
			27
			28
			29
			30
			31
			32
			33
			34
			35
			36
			37
			38
			39
			40
			41
			42
			43
			44
			45
			46
			47
			48
			49
			50
			51
			52
			53
			54
			55
			56
			57
			58
			59
			60
			61
			62
			63
			64
			65
			66
			67
			68
			69
			70
			71
			72
			73
			74
			75
			76
			77
			78
			79
			80
			81
			82
			83
			84
			85
			86
			87
			88
			89
			90
			91
			92
			93
			94
			95
			96
			97
			98
			99

## P_DInAdv
	P_DInAdv: Advanced Discrete Input	Read From CLX:
		Send To CLX:

		Description:		Description for display on HMI	Label for graphic symbol displayed on HMI	Tagname for display on HMI	Process Area for security	Text to display in PV=0 State	Text to display in PV=1 State	1=Disallow selection of Substitute PV	Minimum time Input Sts must maintain state (sec)	1=Display state text in "normal" state (= target), 0=hide (some HMI objects)	1=Tells HMI an object with more info is available	Accelerate Time in Sec	Text to display in Accelerate State	Combine Status Run and Deccelerate as Status Run	Text to display in Decelerate State	Number of decimal places for speed ref/fdbk display (0..6)	Deccelerate Time	Pulse Speed Conversion	Speed Switch Pulse	1 = Used as Speed Switch	Speed Switch Steady 0 = Run	Speed Switch Steady 1 = Run	DIn has Target Disagree Warning & Failure Indication	Speed Switch used with VSD	SpeedSW maintain Sts_Run during Deccelerate	Pulses per Min for Speed Calc	Text to display in Run State	Text to display Units	1 = SpeedSw 0 Run, 2 = SppedSw 1 Run, 4 = SpeedSW Pulse	Always display Symbol else hidden if no error condition	SpeedSwitch TargetDisagree Set Target	SpeedSW status updates only with Motor Run Feedback	VSD Failure indication delay time	VSD Speed Lo Limit for Warn Fail factor adjust	VSD Warning indication delay time	Target Disagree Status Input Condition	Target Disagree Status Gate Condition	Time Inp_Gate must be true before Disagree Status is checked (sec)	Minimum time for Input to disagree with Target to raise Status (sec)	Minimum time for Input to agree with Target to clear Status (sec)	Target Disagree Alarm Condition	Target Disagree Alarm Tag	1=Target Disagree Alarm exists and will be checked	1=Target Disagree Alarm is in latched in, requires Reset Command to clear	1=Target Disagree Alarm must be acknlowledge	Target Disagree Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	Target Disagree Warning Status Input Condition	Target Disagree Warning Status Gate Condition	Time Inp_Gate must be true before Disagree Warning is checked (sec)	Minimum time for Input to disagree with Target to raise Warning (sec)	Minimum time for Input to agree with Target to clear Warning (sec)	Target Disagree Warning Alarm Condition	Target Disagree Warning Alarm Tag	1=Target Disagree Warning Alarm exists and will be checked	1=Target Disagree Warning Alarm is in latched in, requires Reset Command to clear	1=Target Disagree Warning Alarm must be acknlowledge	Target Disagree Warning Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	1=I/O Fault Alarm exists and will be checked	1=Reset required to clear I/O Fault Alarm	1=Acknowledge required for I/O Fault Alarm	I/O Fault Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)
		Usage:		Local	Local	Local	Local	Local	Local	Input	Input	Input	Input	Local	Local	Input	Local	Input	Local	Input	Input	Input	Input	Input	Input	Input	Input	Local	Local	Local	Input	Local	Input	Input	Input	Input	Input	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local
		Data Type:		STRING_40	STRING_20	STRING_20	STRING_Area	STRING_8	STRING_8	BOOL	REAL	BOOL	BOOL	DINT	STRING_8	BOOL	STRING_8	DINT	DINT	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	DINT	STRING_8	STRING_8	SINT	BOOL	BOOL	BOOL	REAL	DINT	REAL	STRING_20	STRING_20	REAL	REAL	REAL	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	REAL	REAL	REAL	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT
			(Origin)	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.TgtDisagreeGate.Cfg_	.TgtDisagreeGate.Cfg_	.TgtDisagreeGate.Cfg_	.TgtDisagreeGate.Cfg_	.TgtDisagreeGate.Cfg_	.TgtDisagree.Cfg_	.TgtDisagree.Cfg_	.TgtDisagree.Cfg_	.TgtDisagree.Cfg_	.TgtDisagree.Cfg_	.TgtDisagree.Cfg_	.TgtDisagree.Cfg_	.TgtDisagree.Cfg_	.TgtDisagree.Cfg_	.TgtDisagree.Cfg_	.TgtDisagreeWarnGate.Cfg_	.TgtDisagreeWarnGate.Cfg_	.TgtDisagreeWarnGate.Cfg_	.TgtDisagreeWarnGate.Cfg_	.TgtDisagreeWarnGate.Cfg_	.TgtDisagreeW.Cfg_	.TgtDisagreeW.Cfg_	.TgtDisagreeW.Cfg_	.TgtDisagreeW.Cfg_	.TgtDisagreeW.Cfg_	.TgtDisagreeW.Cfg_	.TgtDisagreeW.Cfg_	.TgtDisagreeW.Cfg_	.TgtDisagreeW.Cfg_	.TgtDisagreeW.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_
Unit	Tag Description	TagName	Instance	Desc	Label	Tag	Area	0StText	1StText	NoSubstPV	Debounce	NormTextVis	HasMoreObj	AccTime	AcStText	Combine_Sts_RunDec	DcStText	DecPlcs	DecTime	HasPulseSpdConv	HasPulseSSW	HasSSW	HasStdySSWR0	HasStdySSWR1	HasTgtDisWF	HasVSDSpFbk	Maintain_StsRun	PulseMin	RStText	SpeedFdbkEU	SSW_Type	SymbolVis	TgtDisagreeSSWTgt	UseRunFdbkSpdSW	VSD_FailTime	VSD_LoLIM	VSD_WarnTime	InpCond	GateCond	GateDly	OnDly	OffDly	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	InpCond	GateCond	GateDly	OnDly	OffDly	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT
		Default Values:	0	Discrete Input	Discrete Input	P_DIn	area01	Off	On	0	0	1	0	5	'Acc'	0	'Decc'	0	10	0	0	0	0	0	0	0	0	'Run'	'Hz'	0	0	0	0	0	0	0	Target Disagree	Gating Condition	0	0	0	Target Disagree	XA-nnnn	0	0	1	750	1	1	5	480	Target Disagree	Gating Condition	0	0	0	Target Disagree	XA-nnnn	0	0	1	750	1	1	5	480	0	0	1	1000	0	1	5	480
		MyP_DInAdv	1	Advanced Discrete Input	Speed Switch	MyP_DInAdv	area01	Stopped	Running	0	0	1	0	5	'Acc'	0	'Decc'	0	10	0	0	0	0	0	0	0	0	'Run'	'Hz'	0	0	0	0	0	0	0	Target Disagree	Gating Condition	0	0	0	High Vibration	P_DIn.TgtDisagree	1	0	1	3	1	1	5	480	Target Disagree	Gating Condition	0	0	0	High Vibration	P_DIn.TgtDisagree	1	0	1	3	1	1	5	480	0	0	1	1000	1	1	5	480
			2
			3
			4
			5
			6
			7
			8
			9
			10
			11
			12
			13
			14
			15
			16
			17
			18
			19
			20
			21
			22
			23
			24
			25
			26
			27
			28
			29
			30
			31
			32
			33
			34
			35
			36
			37
			38
			39
			40
			41
			42
			43
			44
			45
			46
			47
			48
			49
			50
			51
			52
			53
			54
			55
			56
			57
			58
			59
			60
			61
			62
			63
			64
			65
			66
			67
			68
			69
			70
			71
			72
			73
			74
			75
			76
			77
			78
			79
			80
			81
			82
			83
			84
			85
			86
			87
			88
			89
			90
			91
			92
			93
			94
			95
			96
			97
			98
			99

## P_Dose
	P_Dose: Dosing (Flowmeter / Weigh Scale)	Read From CLX:
		Send To CLX:

		Description:		Description for display on HMI	Label for graphic symbol displayed on HMI	Tagname for display on HMI	Process Area for security	Engineering Units for Quantity for display on HMI	Engineering Units for Rate (flow) for display on HMI	1=differentiate Inp_Qty to get Rate, 0=use Inp_Rate	1=Tells HMI an object with more info is available	Number of decimal places for Rate display (0..6)	1=integrate Inp_Rate to get Quantity, 0=use Inp_Qty	Number of decimal places for Quantity display (0..6)	1=Slow to Dribble before complete, 0=Run full flow until complete	1=Enable automatic adjustment of preact after each delivery	Rate to Quantity EU Multiplier (e.g., Gal to Bbl.)	Quantity Rollover (e.g., max count for pulse input)	Number of Counts in Inp_QtyPV which equal 1.0 EU	Time factor for rate (60 for /min, 3600 for /hr) (sec)	Filter Time Constant (sec) for calculated Rate	Rate below which to report zero flow (Inp_RatePV untis)	Time to allow flow to stop before allowing tolerance check (sec)	Bump (manual top-off) Time (sec)	Percentage of delivery error to auto-adjust preact (%)	Maximum allowed quantity to deliver (setpoint) (EU)	1=Flow reduces quantity (Xfer Out), 0=Flow increases quantity (Xfer In)	Time to pulse Out_Clear to clear external totalizer (sec)	1=Controlled Equipment provides Run (Dribble if used) and Stop Feedback	1=Use run / dribble / stop feedback, 0=Assume equipment state	Time for Equipment Feedback to follow Output before Fault (sec)	1=Stop delivery and Alarm on Equipment Fault; 0=Alarm only on Equipment Fault	Rate at which to deliver when running in Simulation (EU/rate time)	Rate at which to dribble when running in Simulation (EU/rate time)	1=Tells HMI a Channel object (AIChan, etc.) is used for Inp_RatePV	1=Tells HMI a Channel object (AIChan, etc.) is used for Inp_QtyPV	Over Tolerance Alarm Condition	Over Tolerance Alarm Tag	1=Over Tolerance Alarm exists and will be checked	1=Reset required to clear Over Tolerance Alarm	1=Acknowledged required for Over Tolerance Alarm	Over Tolerance Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	Under Tolerance Alarm Condition	Under Tolerance Alarm Tag	1=Under Tolerance Alarm exists and will be checked	1=Reset required to clear Under Tolerance Alarm	1=Acknowledged required for Under Tolerance Alarm	Under Tolerance Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	Zero Fault Alarm Condition	Zero Fault Alarm Tag	1=Zero Fault Alarm exists and will be checked	1=Reset required to clear Zero Fault Alarm	1=Acknowledged required for Zero Fault Alarm	Zero Fault Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	Equipment Fault Alarm Condition	Equipment Fault Alarm Tag	1=Equipment Fault Alarm exists and will be checked	1=Reset required to clear Equipment Fault Alarm	1=Acknowledged required for Equipment Fault Alarm	Equipment Fault Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	1=PSets track OSets in Oper, OSets track PSets in Prog, 0=no tracking	Oper keeps control in Prog or Ext: .0=Reference, .1=Commands	Prog keeps control in Oper or Ext: .0=Reference, .1=Commands	Ext keeps control in Prog or Oper: .0=Reference, .1=Commands	1=Operator (unlocked) exists, can be selected	1=Operator Locked exists, can be selected	1=Program (unlocked) exists, can be selected	1=Program Locked exists, can be selected	1=External exists, can be selected	1=Maintenance exists, can be selected	1=Maintenance Out of Service exists, can be selected	1=Override supersedes Prog/Oper Lock, 0=don't override Lock	1=External supersedes Prog/Oper Lock, 0=don't override Lock	1=Power Up to Prog, 0=Power Up to Oper	Normal Source: 1=Program if no requests; 0=Operator if no requests	Command Priority: 1=Program Cmds Win; 0=Operator Cmds Win	1=PCmd_Prog used as a Level (1=Prog, 0=Oper)	1=PCmd_Lock used as a Level (1=Lock, 0=Unlock)	1=XCmd_Acq used as Level (1=Acq, 0=Rel)
		Usage:		Local	Local	Local	Local	Local	Local	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Local	Local	Local	Local	Local	Local	Local	Local	Input	Input	Input	Input	Local	Local	Local	Local	Local	Local	Local	Local
		Data Type:		STRING_40	STRING_20	STRING_20	STRING_Area	STRING_8	STRING_8	BOOL	BOOL	DINT	BOOL	DINT	BOOL	BOOL	REAL	REAL	REAL	REAL	REAL	REAL	REAL	REAL	REAL	REAL	BOOL	REAL	BOOL	BOOL	REAL	BOOL	REAL	REAL	BOOL	BOOL	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	BOOL	SINT	SINT	SINT	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL
			(Origin)	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.OverTol.Cfg_	.OverTol.Cfg_	.OverTol.Cfg_	.OverTol.Cfg_	.OverTol.Cfg_	.OverTol.Cfg_	.OverTol.Cfg_	.OverTol.Cfg_	.UnderTol.Cfg_	.UnderTol.Cfg_	.UnderTol.Cfg_	.UnderTol.Cfg_	.UnderTol.Cfg_	.UnderTol.Cfg_	.UnderTol.Cfg_	.UnderTol.Cfg_	.ZeroFault.Cfg_	.ZeroFault.Cfg_	.ZeroFault.Cfg_	.ZeroFault.Cfg_	.ZeroFault.Cfg_	.ZeroFault.Cfg_	.ZeroFault.Cfg_	.ZeroFault.Cfg_	.EqpFault.Cfg_	.EqpFault.Cfg_	.EqpFault.Cfg_	.EqpFault.Cfg_	.EqpFault.Cfg_	.EqpFault.Cfg_	.EqpFault.Cfg_	.EqpFault.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_
Unit	Tag Description	TagName	Instance	Desc	Label	Tag	Area	QtyEU	RateEU	CalcRate	HasMoreObj	RateDecPlcs	CalcQty	QtyDecPlcs	HasDribble	AutoAdjPreact	EUQtyMult	Rollover	CountsPerEU	RateTime	RateFiltTC	LoRateCutoff	SettleT	BumpT	AutoAdjPct	MaxQty	LossInQty	ClearPulseT	HasEqpFdbk	UseEqpFdbk	FaultT	ShedOnEqpFault	SimRate	SimDribbleRate	HasChanObjRate	HasChanObjQty	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	SetTrack	OperKeep	ProgKeep	ExtKeep	HasOper	HasOperLocked	HasProg	HasProgLocked	HasExt	HasMaint	HasMOoS	OvrdOverLock	ExtOverLock	ProgPwrUp	ProgNormal	PCmdPriority	PCmdProgAsLevel	PCmdLockAsLevel	ExtAcqAsLevel
		Default Values:	0	Dosing with Flowmeter	Flowmeter Dosing	P_DoseFM	area01	kg	kg/sec	0	0	2	0	2	0	0	1.0	0.0	1.0	1.0	0.1	0.0	1	0.0	10.0	1.50000000e+038	0	1	0	0	10	1	1.0	0.1	0	0	Delivered Too Much	P_DoseFM.OverTol	0	0	1	750	0	1	5	480	Delivered Too Little	P_DoseFM.UnderTol	0	0	1	500	0	1	5	480	Zeroing Meter Failed	P_DoseFM.ZeroFault	0	0	1	1000	0	1	5	480	Equipment Fault	P_DoseFM.EqpFault	0	0	1	1000	0	1	5	480	1	2#0000_0000	2#0000_0000	2#0000_0000	1	1	1	1	0	1	1	1	0	0	0	0	0	0	0
		MyP_DoseFM	1	Dosing with Weigh Scale or Flowmeter	Dosing	P_Dose	area01	kg	kg/sec	0	0	2	0	2	0	0	1	0	1	1	0.100000001490116	0	1	0	10	1.50000000274888E+038	0	1	0	0	10	1	1	0.100000001490116	0	0	Delivery Over Tol	XQADH-nnnn	0	0	1	750	1	1	5	0	Delivery Under Tol	XQADL-nnnn	0	0	1	500	1	1	5	0	Meter Zero Fault	XAF-nnnnA	0	0	1	1000	1	1	5	0	Delivery Equip Fault	XAF-nnnnB	0	0	1	1000	1	1	5	0	1	0	0	0	1	1	1	1	0	1	1	1	0	0	0	0	0	0	0
			2
			3
			4
			5
			6
			7
			8
			9
			10
			11
			12
			13
			14
			15
			16
			17
			18
			19
			20
			21
			22
			23
			24
			25
			26
			27
			28
			29
			30	Strings too long to fit are formatted like this.
			31
			32
			33
			34
			35
			36
			37
			38
			39
			40
			41
			42
			43
			44
			45
			46
			47
			48
			49
			50
			51
			52
			53
			54
			55
			56
			57
			58
			59
			60
			61
			62
			63
			64
			65
			66
			67
			68
			69
			70
			71
			72
			73
			74
			75
			76
			77
			78
			79
			80
			81
			82
			83
			84
			85
			86
			87
			88
			89
			90
			91
			92
			93
			94
			95
			96
			97
			98
			99

## P_DOut
	P_DOut: Discrete Output	Read From CLX:
		Send To CLX:

		Description:		Description for display on HMI	Label for graphic symbol displayed on HMI	Tagname for display on HMI	Process Area for security	Text to display in PV=0 State	Text to display in PV=1 State	Delay before initially turning output ON (sec)	Delay before initially turning output OFF (sec)	Output ON time for Pulse ON or Pulse Continuous	Output OFF time for Pulse OFF or Pulse Continuous	1=Finish Pulse when commanded ON or OFF; 0=switch immediately	1=Enable pulsing functions, 0=On/Off only	1=Device provides an ON feedback signal	1=Device provides an OFF feedback signal	1=Device ON feedback should be used for failure checking	1=Device OFF feedback should be used for failure checking	1=Both feedbacks ON is invalid; 0=Both feedbacks OFF is invalid	1=Go to State 0 and Alarm on Fail to reach position; 0=Alarm only on Fail	1=Go to State 0 and Alarm on I/O Fault; 0=Alarm only on I/O Fault	Delay to echo back of ON/OFF status when in Simulation (sec)	Time to sound audible on commanded start (sec) (0=disabled)	1=Tells HMI a P_Perm is connected to Inp_Perm	1=Tells HMI a P_Intlk is connected to Inp_Intlk	1=Tells HMI an object with more info is available	Time after Output ON to get ON Feedback before Fault (sec)	Fail to Turn On Alarm Condition	Fail to Turn On Alarm Tag	1=Fail to Turn On Alarm exists and will be checked	1=Reset required to clear Fail to Turn ON Alarm	1=Acknowledged required for Fail to Turn ON Alarm	Fail to Turn On Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	Time after Output OFF to get OFF Feedback before Fault (sec)	Fail to Turn Off Alarm Condition	Fail to Turn Off Alarm Tag	1=Fail to Turn Off Alarm exists and will be checked	1=Reset required to clear Fail to Turn OFF Alarm	1=Acknowledged required for Fail to Turn OFF Alarm	Fail to Turn Off Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	Interlock Tripped Alarm Condition	Interlock Tripped Alarm Tag	1=Interlock Tripped Alarm exists and will be checked	1=Reset required to clear Interlock Trip Alarm	1=Acknowledged required for Interlock Trip Alarm	Interlock Tripped Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	I/O Fault Alarm Condition	I/O Fault Alarm Tag	1=I/O Fault Alarm exists and will be checked	1=Reset required to clear I/O Fault Alarm	1=Acknowledged required for I/O Fault Alarm	I/O Fault Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	1=OCmd_Off has priority, accepted any time, 0=OCmd_Off only in Oper, Maint Mode.	1=XCmd_Off any time, 0=XCmd_Off only when Oper selected	1=New device OCmd resets shed latches and cleared alarms, 0=OCmdRest reqd	1=New device XCmd resets shed latches and cleared alarms, 0=XCmdRest reqd	1=Override ignores Bypassable Perm/ Intlk; 0=always use Perm/Intlk	1=Operator (unlocked) exists, can be selected	1=Operator Locked exists, can be selected	1=Program (unlocked) exists, can be selected	1=Program Locked exists, can be selected	1=External exists, can be selected	1=Maintenance exists, can be selected	1=Maintenance Out of Service exists, can be selected	1=Override supersedes Prog/Oper Lock, 0=don't override Lock	1=External supersedes Prog/Oper Lock, 0=don't override Lock	1=Power Up to Prog, 0=Power Up to Oper	Normal Source: 1=Program if no requests; 0=Operator if no requests	Command Priority: 1=Program Cmds Win; 0=Operator Cmds Win	1=PCmd_Prog used as a Level (1=Prog, 0=Oper)	1=PCmd_Lock used as a Level (1=Lock, 0=Unlock)	1=XCmd_Acq used as Level (1=Acq, 0=Rel)	0 = Horn on energize only, 1 = Horn on any state change
		Usage:		Local	Local	Local	Local	Local	Local	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Local	Local	Local	Local	Local	Local	Local	Local	Input	Local	Local	Local	Local	Local	Local	Local	Local	Input	Input	Input	Input	Input	Local	Local	Local	Local	Local	Local	Local	Local	Input
		Data Type:		STRING_40	STRING_20	STRING_20	STRING_Area	STRING_8	STRING_8	REAL	REAL	REAL	REAL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	REAL	REAL	BOOL	BOOL	BOOL	REAL	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	REAL	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL
			(Origin)	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.OnFail.Cfg_	.OnFail.Cfg_	.OnFail.Cfg_	.OnFail.Cfg_	.OnFail.Cfg_	.OnFail.Cfg_	.OnFail.Cfg_	.OnFail.Cfg_	.Cfg_	.OffFail.Cfg_	.OffFail.Cfg_	.OffFail.Cfg_	.OffFail.Cfg_	.OffFail.Cfg_	.OffFail.Cfg_	.OffFail.Cfg_	.OffFail.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.Cfg_
Unit	Tag Description	TagName	Instance	Desc	Label	Tag	Area	0StText	1StText	OnDelayT	OffDelayT	OnPulseT	OffPulseT	CompletePulse	HasPulse	HasOnFdbk	HasOffFdbk	UseOnFdbk	UseOffFdbk	FdbkFail	ShedOnFail	ShedOnIOFault	SimFdbkT	StartHornT	HasPermObj	HasIntlkObj	HasMoreObj	OnFailT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	OffFailT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	OperOffPrio	ExtOffPrio	OCmdResets	XCmdResets	OvrdPermIntlk	HasOper	HasOperLocked	HasProg	HasProgLocked	HasExt	HasMaint	HasMOoS	OvrdOverLock	ExtOverLock	ProgPwrUp	ProgNormal	PCmdPriority	PCmdProgAsLevel	PCmdLockAsLevel	ExtAcqAsLevel	HornOnChange
		Default Values:	0	Discrete On/Off Device	Discrete Device	P_DOut	area01	Off	On	0.0	0.0	0.5	0.5	0	0	0	0	0	0	0	1	1	2	0	0	0	0	0	10	Failed to Turn On	P_DOut.OnFail	0	0	1	1000	0	1	5	480	10	Failed to Turn Off	P_DOut.OffFail	0	0	1	1000	0	1	5	480	Interlock Trip	P_DOut.IntlkTrip	0	0	1	500	0	1	5	480	I/O Fault	P_DOut.IOFault	0	0	1	1000	0	1	5	480	0	0	0	0	0	1	1	1	1	0	1	1	1	0	0	0	0	0	0	0
		MyP_DOut	1	Discrete On/Off Device	Discrete Device	P_DOut	area01	Off	On	0	0	0	0	0	0	0	0	1	1	0	0	0	0	0	1	Failed to Turn On	0	0	0	0	1	1	1	1	4	4	Failed to Turn Off	4	0	0	0	2	1	1	10	5	Interlock Trip	5	1	1	1	3	1	1	5	480	I/O Fault		1	0	1	3	1	1	5	480	0	0	0	0	0	1	1	1	1	0	1	1	1	0	0	0	0	0	0	0
			2
			3
			4
			5
			6
			7
			8
			9
			10
			11
			12
			13
			14
			15
			16
			17
			18
			19
			20
			21
			22
			23
			24
			25
			26
			27
			28
			29
			30	Strings too long to fit are formatted like this.
			31
			32
			33
			34
			35
			36
			37
			38
			39
			40
			41
			42
			43
			44
			45
			46
			47
			48
			49
			50
			51
			52
			53
			54
			55
			56
			57
			58
			59
			60
			61
			62
			63
			64
			65
			66
			67
			68
			69
			70
			71
			72
			73
			74
			75
			76
			77
			78
			79
			80
			81
			82
			83
			84
			85
			86
			87
			88
			89
			90
			91
			92
			93
			94
			95
			96
			97
			98
			99

## P_E1PlusE
	P_E1PlusE: E1 Plus Overload Relay (EtherNet/IP)	Read From CLX:
		Send To CLX:

		Description:		Description for display on HMI	Label for graphic symbol displayed on HMI	Tagname for display on HMI	Process Area for security	Text for Input #1 label	Text for Input #2 label	Text for Output A label	1=Trip Reset function is available to operator	1=Trip Reset function is available to Maintenance	Time (sec) to pulse Trip Reset or Remote Trip output to E3	No more than (1,2,3) remote Trip Resets are allowed in this amount of time (sec)	No more than this many remote Trip Resets are allowed in (cfgd) time	1=Tells HMI an object with more info is available	1= Acknowledge required for I/O Fault Alarm	Alarm: I/O Fault	Alarm: I/O Fault	Alarm: I/O Fault	Alarm: I/O Fault	1=I/O Fault exists and will be checked	Alarm: I/O Fault	1= Reset required to clear I/O Fault Alarm	I/O Fault Alarm Severity 1=info 2=warn 3=excep 4=fault	Alarm: I/O Fault	1= Acknowledge required for Trip Alarm	Alarm: Overload has tripped	Alarm: Overload has tripped	Alarm: Overload has tripped	Alarm: Overload has tripped	1= Trip Alarm exists and will be checked	Alarm: Overload has tripped	1= Reset required to clear Trip Alarm	I/O Fault Alarm Severity 1=info 2=warn 3=excep 4=fault	Alarm: Overload has tripped	1=Acknowledge required for Warning Alarm	Alarm: Warning of impending trip	Alarm: Warning of impending trip	Alarm: Warning of impending trip	Alarm: Warning of impending trip	1=Warning Alarm exists and will be checked	Alarm: Warning of impending trip	Alarm: Warning of impending trip	Warning Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	Alarm: Warning of impending trip
		Usage:		Local	Local	Local	Local	Local	Local	Local	Input	Input	Input	Input	Input	Input	Local	Local	Local	Local	Local	Local	Local	Local
		Data Type:		STRING_40	STRING_20	STRING_20	STRING_Area	STRING_20	STRING_20	STRING_20	BOOL	BOOL	REAL	REAL	DINT	BOOL	BOOL	BOOL	BOOL	DINT	STRING_20	BOOL	DINT	BOOL	DINT	STRING_20	BOOL	BOOL	BOOL	DINT	STRING_20	BOOL	DINT	BOOL	DINT	STRING_20	BOOL	BOOL	BOOL	DINT	STRING_20	BOOL	DINT	BOOL	DINT	STRING_20
			(Origin)	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.Trip.Cfg_	.Trip.Cfg_	.Trip.Cfg_	.Trip.Cfg_	.Trip.Cfg_	.Trip.Cfg_	.Trip.Cfg_	.Trip.Cfg_	.Warn.Cfg_	.Warn.Cfg_	.Warn.Cfg_	.Warn.Cfg_	.Warn.Cfg_	.Warn.Cfg_	.Warn.Cfg_	.Warn.Cfg_
Unit	Tag Description	TagName	Instance	Desc	Label	Tag	Area	Inp1Txt	Inp2Txt	OutATxt	AllowOperReset	AllowMaintReset	PulseT	LocalResetReqdT	LocalResetReqdNum	HasMoreObj	AckReqd	AllowDisable	AllowShelve	AlmMinOnT	Cond	Exists	MaxShelfT	ResetReqd	Severity	Tag	AckReqd	AllowDisable	AllowShelve	AlmMinOnT	Cond	Exists	MaxShelfT	ResetReqd	Severity	Tag	AckReqd	AllowDisable	AllowShelve	AlmMinOnT	Cond	Exists	MaxShelfT	ResetReqd	Severity	Tag
		Default Values:	0	Motor Overload Relay	Overload	P_E1PlusE	area01	Run Feedback		Starter Energized	0	1	5	3600	3	0	1	1	1	5	I/O Fault	0	480	0	1000	IAF-nnnn	1	1	1	5	Overload Tripped	0	480	0	750	IAHH_nnnn	1	1	1	5	Overload Warning	0	480	0	500	IAH-nnnn
		P181_Ovld	1	Motor Overload Relay	Overload Relay	P_E3Ovld	area01	Run Feedback	Disconnect Closed	Starter Energized	1	1	5	3600	3	0	0	1	1	5	I/O Fault	0	480	0	0	P_Alarm	0	1	1	5	Overload Trip	0	480	0	0	P_Alarm	0	1	1	5	Overload Warning	0	480	0	0	P_Alarm
			2
			3
			4
			5
			6
			7
			8
			9
			10
			11
			12
			13
			14
			15
			16
			17
			18
			19
			20
			21
			22
			23
			24
			25
			26
			27
			28
			29
			30
			31
			32
			33
			34
			35
			36
			37
			38
			39
			40
			41
			42
			43
			44
			45
			46
			47
			48
			49
			50
			51
			52
			53
			54
			55
			56
			57
			58
			59
			60
			61
			62
			63
			64
			65
			66
			67
			68
			69
			70
			71
			72
			73
			74
			75
			76
			77
			78
			79
			80
			81
			82
			83
			84
			85
			86
			87
			88
			89
			90

## P_E300Ovld
	P_E300Ovld: E300 Overload Relay (EtherNet/IP)	Read From CLX:
		Send To CLX:

		Description:		Description for display on HMI	Label for graphic symbol displayed on HMI	Tagname for display on HMI	Process Area for security	Text for Discrete Input Pt00 label	Text for Discrete Input Pt01 label	Text for Discrete Input Pt02 label	Text for Discrete Input Pt03 label	Text for Discrete Input Pt04 label	Text for Discrete Input Pt05 label	Text for Discrete Output Pt00 label	Text for Discrete Output Pt01 label	Text for Discrete Output Pt02 label	1=Remote Trip function is available to Operator	1=Trip Reset function is available to operator	1=Remote Trip function is available to Maintenance	1=Trip Reset function is available to Maintenance	Time (sec) to pulse Trip Reset or Remote Trip output to E3	No more than (1..3) remote Trip Resets are allowed in this amount of time (sec)	No more than this many remote Trip Resets are allowed in (cfgd) time (1..3)	1=Tells HMI an object with more info is available	1=Acknowledge required for I/O Fault Alarm	Alarm: I/O Fault	Alarm: I/O Fault	Alarm: I/O Fault	Alarm: I/O Fault	1=I/O Fault Alarm exists and will be checked	Alarm: I/O Fault	1=Reset required to clear I/O Fault Alarm	I/O Fault Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	Alarm: I/O Fault	1=Acknowledge required for Trip Alarm	Alarm: Overload has tripped	Alarm: Overload has tripped	Alarm: Overload has tripped	Alarm: Overload has tripped	1=Trip Alarm exists and will be checked	Alarm: Overload has tripped	1=Reset required to clear Trip Alarm	Trip Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	Alarm: Overload has tripped	1=Acknowledge required for Warning Alarm	Alarm: Warning of impending trip	Alarm: Warning of impending trip	Alarm: Warning of impending trip	Alarm: Warning of impending trip	1=Warning Alarm exists and will be checked	Alarm: Warning of impending trip	1=Reset required to clear Warning Alarm	Warning Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	Alarm: Warning of impending trip
		Usage:		Local	Local	Local	Local	Local	Local	Local	Local	Input	Input	Input	Input	Input	Input	Input	Input	Local	Local	Local	Local	Local	Local	Local	Local
		Data Type:		STRING_40	STRING_20	STRING_20	STRING_Area	STRING_20	STRING_20	STRING_20	STRING_20	STRING_20	STRING_20	STRING_20	STRING_20	BOOL	BOOL	BOOL	BOOL	REAL	REAL	DINT	BOOL	BOOL	BOOL	BOOL	DINT	STRING_20	BOOL	DINT	BOOL	DINT	STRING_20	BOOL	BOOL	BOOL	DINT	STRING_20	BOOL	DINT	BOOL	DINT	STRING_20	BOOL	BOOL	BOOL	DINT	STRING_20	BOOL	DINT	BOOL	DINT	STRING_20
			(Origin)	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.Trip.Cfg_	.Trip.Cfg_	.Trip.Cfg_	.Trip.Cfg_	.Trip.Cfg_	.Trip.Cfg_	.Trip.Cfg_	.Trip.Cfg_	.Warn.Cfg_	.Warn.Cfg_	.Warn.Cfg_	.Warn.Cfg_	.Warn.Cfg_	.Warn.Cfg_	.Warn.Cfg_	.Warn.Cfg_
Unit	Tag Description	TagName	Instance	Desc	Label	Tag	Area	InpPt00Txt	InpPt01Txt	InpPt02Txt	InpPt03Txt	InpPt04Txt	InpPt05Txt	OutPt00Txt	OutPt01Txt	OutPt02Txt	AllowOperTrip	AllowOperReset	AllowMaintTrip	AllowMaintReset	PulseT	LocalResetReqdT	LocalResetReqdNum	HasMoreObj	AckReqd	AllowDisable	AllowShelve	AlmMinOnT	Cond	Exists	MaxShelfT	ResetReqd	Severity	Tag	AckReqd	AllowDisable	AllowShelve	AlmMinOnT	Cond	Exists	MaxShelfT	ResetReqd	Severity	Tag	AckReqd	AllowDisable	AllowShelve	AlmMinOnT	Cond	Exists	MaxShelfT	ResetReqd	Severity	Tag
		Default Values:	0	Motor Overload Relay	Overload Relay	P_E300Ovld	area01	Starter Aux Contact					0	0	0	1	5	3600	3	0	1	1	1	5	I/O Fault	0	480	0	1000	IAF-nnnn	1	1	1	5	Overload Tripped	0	480	0	750	IAHH_nnnn	1	1	1	5	Overload Warning	0	480	0	500	IAH-nnnn
		P182_Ovld	1	Motor Overload Relay	Overload Relay	P_E300Ovld	area01	Starter Aux Contact					Starter Energized			0	0	1	1	5	3600	3	0	1	1	1	5	I/O Fault	0	480	0	4	IAF-nnnn	1	1	1	5	Overload Trip	0	480	0	3	P_Alarm	1	1	1	5	Overload Warning	0	480	0	2	IAH-nnnn
			2
			3
			4
			5
			6
			7
			8
			9
			10
			11
			12
			13
			14
			15
			16
			17
			18
			19
			20
			21
			22
			23
			24
			25
			26
			27
			28
			29
			30
			31
			32
			33
			34
			35
			36
			37
			38
			39
			40
			41
			42
			43
			44
			45
			46
			47
			48
			49
			50
			51
			52
			53
			54
			55
			56
			57
			58
			59
			60
			61
			62
			63
			64
			65
			66
			67
			68
			69
			70
			71
			72
			73
			74
			75
			76
			77
			78
			79
			80
			81
			82
			83
			84
			85
			86
			87
			88
			89
			90

## P_E3Ovld
	P_E3Ovld: E3 / E3Plus Overload Relay	Read From CLX:
		Send To CLX:

		Description:		Description for display on HMI	Label for graphic symbol displayed on HMI	Tagname for display on HMI	Process Area for security	Text for Input #1 label	Text for Input #2 label	Text for Input #3 label (E3Plus only)	Text for Input #4 label (E3Plus only)	Text for Input #5 label (-EC5 only)	Text for Input #6 label (-EC5 only)	Text for Output A label	Text for Output B label (E3Plus only)	1=Remote Trip function is available to Operator	1=Trip Reset function is available to operator	1=Remote Trip function is available to Maintenance	1=Trip Reset function is available to Maintenance	Time (sec) to pulse Trip Reset or Remote Trip output to E3	No more than (1,2,3) remote Trip Resets are allowed in this amount of time (sec)	No more than this many remote Trip Resets are allowed in (cfgd) time	1=Tells HMI an object with more info is available	1=Acknowledge required for I/O Fault Alarm	Alarm: I/O Fault	Alarm: I/O Fault	Alarm: I/O Fault	Alarm: I/O Fault	1=I/O Fault Alarm exists and will be checked	Alarm: I/O Fault	1=Reset required to clear I/O Fault Alarm	I/O Fault Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	Alarm: I/O Fault	1=Acknowledge required for Trip Alarm	Alarm: Overload has tripped	Alarm: Overload has tripped	Alarm: Overload has tripped	Alarm: Overload has tripped	1=Trip Alarm exists and will be checked	Alarm: Overload has tripped	1=Reset required to clear Trip Alarm	Trip Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	Alarm: Overload has tripped	1=Acknowledge required for Warning Alarm	Alarm: Warning of impending trip	Alarm: Warning of impending trip	Alarm: Warning of impending trip	Alarm: Warning of impending trip	1=Warning Alarm exists and will be checked	Alarm: Warning of impending trip	1=Reset required to clear Warning Alarm	Warning Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	Alarm: Warning of impending trip
		Usage:		Local	Local	Local	Local	Local	Local	Local	Local	Input	Input	Input	Input	Input	Input	Input	Input	Local	Local	Local	Local	Local	Local	Local	Local
		Data Type:		STRING_40	STRING_20	STRING_20	STRING_Area	STRING_20	STRING_20	STRING_20	STRING_20	STRING_20	STRING_20	STRING_20	STRING_20	BOOL	BOOL	BOOL	BOOL	REAL	REAL	DINT	BOOL	BOOL	BOOL	BOOL	DINT	STRING_20	BOOL	DINT	BOOL	DINT	STRING_20	BOOL	BOOL	BOOL	DINT	STRING_20	BOOL	DINT	BOOL	DINT	STRING_20	BOOL	BOOL	BOOL	DINT	STRING_20	BOOL	DINT	BOOL	DINT	STRING_20
			(Origin)	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.Trip.Cfg_	.Trip.Cfg_	.Trip.Cfg_	.Trip.Cfg_	.Trip.Cfg_	.Trip.Cfg_	.Trip.Cfg_	.Trip.Cfg_	.Warn.Cfg_	.Warn.Cfg_	.Warn.Cfg_	.Warn.Cfg_	.Warn.Cfg_	.Warn.Cfg_	.Warn.Cfg_	.Warn.Cfg_
Unit	Tag Description	TagName	Instance	Desc	Label	Tag	Area	Inp1Txt	Inp2Txt	Inp3Txt	Inp4Txt	Inp5Txt	Inp6Txt	OutATxt	OutBTxt	AllowOperTrip	AllowOperReset	AllowMaintTrip	AllowMaintReset	PulseT	LocalResetReqdT	LocalResetReqdNum	HasMoreObj	AckReqd	AllowDisable	AllowShelve	AlmMinOnT	Cond	Exists	MaxShelfT	ResetReqd	Severity	Tag	AckReqd	AllowDisable	AllowShelve	AlmMinOnT	Cond	Exists	MaxShelfT	ResetReqd	Severity	Tag	AckReqd	AllowDisable	AllowShelve	AlmMinOnT	Cond	Exists	MaxShelfT	ResetReqd	Severity	Tag
		Default Values:	0	Motor Overload Relay	Overload Relay	P_E3Ovld	area01	Run Feedback	Disconnect Closed					Starter Energized		0	0	0	0	5	3600	3	0	1	1	1	5	I/O Fault	0	480	0	1000	IAF-nnnn	1	1	1	5	Overload Tripped	1	480	0	750	IAHH_nnnn	1	1	1	5	Overload Warning	0	480	0	500	IAH-nnnn
		P180_Ovld	1	Motor Overload Relay	Overload Relay	P_E3Ovld	area01	Run Feedback	Disconnect Closed					Starter Energized		1	1	1	1	5	3600	3	0	1	1	1	5	I/O Fault	1	480	0	3	P_Alarm	1	1	1	5	Overload Trip	1	480	0	3	P_Alarm	1	1	1	5	Overload Warning	1	480	0	3	P_Alarm
			2
			3
			4
			5
			6
			7
			8
			9
			10
			11
			12
			13
			14
			15
			16
			17
			18
			19
			20
			21
			22
			23
			24
			25
			26
			27
			28
			29
			30
			31
			32
			33
			34
			35
			36
			37
			38
			39
			40
			41
			42
			43
			44
			45
			46
			47
			48
			49
			50
			51
			52
			53
			54
			55
			56
			57
			58
			59
			60
			61
			62
			63
			64
			65
			66
			67
			68
			69
			70
			71
			72
			73
			74
			75
			76
			77
			78
			79
			80
			81
			82
			83
			84
			85
			86
			87
			88
			89
			90

## P_Fanout
	P_Fanout: Analog Fanout	Read From CLX:
		Send To CLX:

		Description:		Description for display on HMI	Label for graphic symbol displayed on HMI	Tagname for display on HMI	Process Area for security	Engineering Units for display on HMI	Input CV Minimum Engineering Units (for scaling)	Input CV Maximum Engineering Units (for scaling)	Input CV Minimum (Lo Clamp) (Inp EU)	Input CV Maximum (Hi Clamp) (Ino EU)	Program Setting for Input CV Rate of Change Limit (inc or dec) (Inp EU/sec)	Fixed Initialization value (in Inp_CV eng. units), used if Cfg_UseFixedInit=1	1=Use Cfg_FixedInitVal to initialize primary, 0=Use Inp_CV1InitVal	1=Hold Output on Inf / NaN Input, 0=Copy Inf / NaN through	1=Tells HMI an object with more info is available	1=Tells HMI to enable navigation to a connected input CV object	Tagname for destination of input CV Navigation button	Number of decimal places for CV display (0..6)	Sets bits indicate which Navigation buttons are enabled .0=CV1, .1=CV2, ….7=CV8	Tagname for destinations CV of Navigation button	Output 1 Engineering Units for display on HMI	Output 1 Label for display on HMI	Configuration (hidden) for CV2 Ratio (m in mx+b)	Configuration (hidden) for CV1 Offset (b in mx+b)	Output CV #1 Minimum in Engineering Units (for clamping)	Output CV #1 Maximum in Engineering Units (for clamping)	Rate (EU/sec) which CV1 Bias is taken up after CV1InitReq = 0	Sets bits indicate which Navigation buttons are enabled .0=CV1, .1=CV2, ….7=CV8	Tagname for destinations CV1 of Navigation button	1=Output CV #2 is connected	Output 2 Engineering Units for display on HMI	Output 2 Label for display on HMI	Configuration (hidden) for CV2 Ratio (m in mx+b)	Configuration (hidden) for CV2 Offset (b in mx+b)	Output CV #2 Minimum in Engineering Units (for clamping)	Output CV #2 Maximum in Engineering Units (for clamping)	Rate (EU/sec) which CV2 Bias is taken up after CV2InitReq = 0	Sets bits indicate which Navigation buttons are enabled .0=CV1, .1=CV2, ….7=CV8	Tagname for destinations CV2 of Navigation button	1=Output CV #3 is connected	Output 3 Engineering Units for display on HMI	Output 3 Label for display on HMI	Configuration (hidden) for CV3 Ratio (m in mx+b)	Configuration (hidden) for CV3 Offset (b in mx+b)	Output CV #3 Minimum in Engineering Units (for clamping)	Output CV #3 Maximum in Engineering Units (for clamping)	Rate (EU/sec) which CV3 Bias is taken up after CV3InitReq = 0	Sets bits indicate which Navigation buttons are enabled .0=CV1, .1=CV2, ….7=CV8	Tagname for destinations CV3 of Navigation button	1=Output CV #4 is connected	Output 4 Engineering Units for display on HMI	Output 4 Label for display on HMI	Configuration (hidden) for CV4 Ratio (m in mx+b)	Configuration (hidden) for CV4 Offset (b in mx+b)	Output CV #4 Minimum in Engineering Units (for clamping)	Output CV #4 Maximum in Engineering Units (for clamping)	Rate (EU/sec) which CV4 Bias is taken up after CV4InitReq = 0	Sets bits indicate which Navigation buttons are enabled .0=CV1, .1=CV2, ….7=CV8	Tagname for destinations CV4 of Navigation button	1=Output CV #5 is connected	Output 5 Engineering Units for display on HMI	Output 5 Label for display on HMI	Configuration (hidden) for CV5 Ratio (m in mx+b)	Configuration (hidden) for CV5 Offset (b in mx+b)	Output CV #5 Minimum in Engineering Units (for clamping)	Output CV #5 Maximum in Engineering Units (for clamping)	Rate (EU/sec) which CV5 Bias is taken up after CV5InitReq = 0	Sets bits indicate which Navigation buttons are enabled .0=CV1, .1=CV2, ….7=CV8	Tagname for destinations CV5 of Navigation button	1=Output CV #6 is connected	Output 6 Engineering Units for display on HMI	Output 6 Label for display on HMI	Configuration (hidden) for CV6 Ratio (m in mx+b)	Configuration (hidden) for CV6 Offset (b in mx+b)	Output CV #6 Minimum in Engineering Units (for clamping)	Output CV #6 Maximum in Engineering Units (for clamping)	Rate (EU/sec) which CV6 Bias is taken up after CV6InitReq = 0	Sets bits indicate which Navigation buttons are enabled .0=CV1, .1=CV2, ….7=CV8	Tagname for destinations CV6 of Navigation button	1=Output CV #7 is connected	Output 7 Engineering Units for display on HMI	Output 7 Label for display on HMI	Configuration (hidden) for CV7 Ratio (m in mx+b)	Configuration (hidden) for CV7 Offset (b in mx+b)	Output CV #7 Minimum in Engineering Units (for clamping)	Output CV #7 Maximum in Engineering Units (for clamping)	Rate (EU/sec) which CV7 Bias is taken up after CV7InitReq = 0	Sets bits indicate which Navigation buttons are enabled .0=CV1, .1=CV2, ….7=CV8	Tagname for destinations CV7 of Navigation button	1=Output CV #8 is connected	Output 8 Engineering Units for display on HMI	Output 8 Label for display on HMI	Configuration (hidden) for CV8 Ratio (m in mx+b)	Configuration (hidden) for CV8 Offset (b in mx+b)	Output CV #8 Minimum in Engineering Units (for clamping)	Output CV #8 Maximum in Engineering Units (for clamping)	Rate (EU/sec) which CV8 Bias is taken up after CV8InitReq = 0
		Usage:		Local	Local	Local	Local	Local	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Local	Input	Input		Local	Local	Input	Input	Input	Input	Input	Input		Input	Local	Local	Input	Input	Input	Input	Input	Input		Input	Local	Local	Input	Input	Input	Input	Input	Input		Input	Local	Local	Input	Input	Input	Input	Input	Input		Input	Local	Local	Input	Input	Input	Input	Input	Input		Input	Local	Local	Input	Input	Input	Input	Input	Input		Input	Local	Local	Input	Input	Input	Input	Input	Input		Input	Local	Local	Input	Input	Input	Input	Input
		Data Type:		STRING_40	STRING_20	STRING_20	STRING_Area	STRING_8	REAL	REAL	REAL	REAL	REAL	REAL	BOOL	BOOL	BOOL	BOOL	STRING_NavTag	DINT	BIT	STRING_NavTag	STRING_8	STRING_20	REAL	REAL	REAL	REAL	REAL	BIT	STRING_NavTag	BOOL	STRING_8	STRING_20	REAL	REAL	REAL	REAL	REAL	BIT	STRING_NavTag	BOOL	STRING_8	STRING_20	REAL	REAL	REAL	REAL	REAL	BIT	STRING_NavTag	BOOL	STRING_8	STRING_20	REAL	REAL	REAL	REAL	REAL	BIT	STRING_NavTag	BOOL	STRING_8	STRING_20	REAL	REAL	REAL	REAL	REAL	BIT	STRING_NavTag	BOOL	STRING_8	STRING_20	REAL	REAL	REAL	REAL	REAL	BIT	STRING_NavTag	BOOL	STRING_8	STRING_20	REAL	REAL	REAL	REAL	REAL	BIT	STRING_NavTag	BOOL	STRING_8	STRING_20	REAL	REAL	REAL	REAL	REAL
			(Origin)	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_
Unit	Tag Description	TagName	Instance	Desc	Label	Tag	Area	CV_EU	CVEUMin	CVEUMax	CVMin	CVMax	CVRoCLim	FixedInitVal	UseFixedInit	ShedHold	HasMoreObj	HasCVNav	CVNavTag	CVDecPlcs	HasNav.0	NavTag[0]	CV1_EU	CV1_Label	CV1Ratio	CV1Offset	CV1Min	CV1Max	CV1TakeupRate	HasNav.1	NavTag[1]	HasCV2	CV2_EU	CV2_Label	CV2Ratio	CV2Offset	CV2Min	CV2Max	CV2TakeupRate	HasNav.2	NavTag[2]	HasCV3	CV3_EU	CV3_Label	CV3Ratio	CV3Offset	CV3Min	CV3Max	CV3TakeupRate	HasNav.3	NavTag[3]	HasCV4	CV4_EU	CV4_Label	CV4Ratio	CV4Offset	CV4Min	CV4Max	CV4TakeupRate	HasNav.4	NavTag[4]	HasCV5	CV5_EU	CV5_Label	CV5Ratio	CV5Offset	CV5Min	CV5Max	CV5TakeupRate	HasNav.5	NavTag[5]	HasCV6	CV6_EU	CV6_Label	CV6Ratio	CV6Offset	CV6Min	CV6Max	CV6TakeupRate	HasNav.6	NavTag[6]	HasCV7	CV7_EU	CV7_Label	CV7Ratio	CV7Offset	CV7Min	CV7Max	CV7TakeupRate	HasNav.7	NavTag[7]	HasCV8	CV8_EU	CV8_Label	CV8Ratio	CV8Offset	CV8Min	CV8Max	CV8TakeupRate
		Default Values:	0	Analog Fanout	Analog Fanout	P_Fanout	area01	%	0.0	100.0	0.0	100.0	0	0.0	0	0	0	0		0	0		%	Output 1	-2	100	0.0	100	1.0	0		1	%	Output 2	2	-100	0.0	100.0	1.0	0		0	%	Output 3	1.0	0.0	0.0	100.0	1.0	0		0	%	Output 4	1.0	0.0	0.0	100.0	1.0	0		0	%	Output 5	1.0	0.0	0.0	100.0	1.0	0		0	%	Output 6	1.0	0.0	0.0	100.0	1.0	0		0	%	Output 7	1.0	0.0	0.0	100.0	1.0	0		0	%	Output 8	1.0	0.0	0.0	100.0	1.0
		MyP_Fanout	1	Analog Fanout	Analog Fanout	P_Fanout	area01	%	0	100	0	100	0	0	0	0	0	0		0	0		Output 5	%	2	-100	0	0	0	1		0	0	0	0	0	0	0	0	0		0	0	0	0	0	0	0	0	1		0	0	100	100	2	-100	0	100	1		1	0	100	1	0	1	100	0.5	1		1	1	1	1	0	-20	20	0	1		1	80	0	1	0	0	100	1	1		0			-1	120	0	100	1
			2
			3
			4
			5
			6
			7
			8
			9
			10
			11
			12
			13
			14
			15
			16
			17
			18
			19
			20
			21
			22
			23
			24
			25
			26
			27
			28
			29
			30	Strings too long to fit are formatted like this.
			31
			32
			33
			34
			35
			36
			37
			38
			39
			40
			41
			42
			43
			44
			45
			46
			47
			48
			49
			50
			51
			52
			53
			54
			55
			56
			57
			58
			59
			60
			61
			62
			63
			64
			65
			66
			67
			68
			69
			70
			71
			72
			73
			74
			75
			76
			77
			78
			79
			80
			81
			82
			83
			84
			85
			86
			87
			88
			89
			90
			91
			92
			93
			94
			95
			96
			97
			98
			99

## P_HiLoSel
	P_HiLoSel: High-Select or Low-Select	Read From CLX:
		Send To CLX:

		Description:		Description for display on HMI	Label for graphic symbol displayed on HMI	Tagname for display on HMI	Process Area for security	Engineering Units for display on HMI	Selection: 1=High-Select, 0=Low-Select	Minimum Inp to output	Maximum Inp to output	Number of decimal places for CV display (0..6)	1=Tells HMI an object with more info is available	1=Tells HMI to enable navigation to a connected output Output object	Tagname for destination of output Navigation button	Inp Input 1 Label for display on HMI	1 = Inp_Inp1 is connected	1 = Inp_Inp1 is included in selection (for Maintenance use)	1 = Use Inp1Init = InpSel +/- Kp1*E1 Offset, 0 = no Offset	Sets bits indicate which Navigation buttons are enabled .0=Inp1, .1=Inp2, ….5=Inp6	Tagname for destination of navigation button for Inp Input 1	Inp Input 2 Label for display on HMI	1 = Inp_Inp2 is connected	1 = Inp_Inp2 is included in selection (for Maintenance use)	1 = Use Inp2Init = InpSel +/- Kp2*E2 Offset, 0 = no Offset	Sets bits indicate which Navigation buttons are enabled .0=Inp1, .1=Inp2, ….5=Inp6	Tagname for destination of navigation button for Inp Input 2	Inp Input 3 Label for display on HMI	1 = Inp_Inp3 is connected	1 = Inp_Inp3 is included in selection (for Maintenance use)	1 = Use Inp3Init = InpSel +/- Kp3*E3 Offset, 0 = no Offset	Sets bits indicate which Navigation buttons are enabled .0=Inp1, .1=Inp2, ….5=Inp6	Tagname for destination of navigation button for Inp Input 3	Inp Input 4 Label for display on HMI	1 = Inp_Inp4 is connected	1 = Inp_Inp4 is included in selection (for Maintenance use)	1 = Use Inp4Init = InpSel +/- Kp4*E4 Offset, 0 = no Offset	Sets bits indicate which Navigation buttons are enabled .0=Inp1, .1=Inp2, ….5=Inp6	Tagname for destination of navigation button for Inp Input 4	Inp Input 5 Label for display on HMI	1 = Inp_Inp5 is connected	1 = Inp_Inp5 is included in selection (for Maintenance use)	1 = Use Inp5Init = InpSel +/- Kp5*E5 Offset, 0 = no Offset	Sets bits indicate which Navigation buttons are enabled .0=Inp1, .1=Inp2, ….5=Inp6	Tagname for destination of navigation button for Inp Input 5	Inp Input 6 Label for display on HMI	1 = Inp_Inp6 is connected	1 = Inp_Inp6 is included in selection (for Maintenance use)	1 = Use Inp6Init = InpSel +/- Kp6*E6 Offset, 0 = no Offset	Sets bits indicate which Navigation buttons are enabled .0=Inp1, .1=Inp2, ….5=Inp6	Tagname for destination of navigation button for Inp Input 6
		Usage:		Local	Local	Local	Local	Local	Input	Input	Input	Input	Input	Input	Local	Local	Input	Input	Input	Input		Local	Input	Input	Input	Input		Local	Input	Input	Input	Input		Local	Input	Input	Input	Input		Local	Input	Input	Input	Input		Local	Input	Input	Input	Input
		Data Type:		STRING_40	STRING_20	STRING_20	STRING_Area	STRING_8	BOOL	REAL	REAL	DINT	BOOL	BOOL	STRING_NavTag	STRING_20	BOOL	BOOL	BOOL	BIT	STRING_NavTag	STRING_20	BOOL	BOOL	BOOL	BIT	STRING_NavTag	STRING_20	BOOL	BOOL	BOOL	BIT	STRING_NavTag	STRING_20	BOOL	BOOL	BOOL	BIT	STRING_NavTag	STRING_20	BOOL	BOOL	BOOL	BIT	STRING_NavTag	STRING_20	BOOL	BOOL	BOOL	BIT	STRING_NavTag
			(Origin)	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_
Unit	Tag Description	TagName	Instance	Desc	Label	Tag	Area	EU	HiLoSel	OutMin	OutMax	DecPlcs	HasMoreObj	HasOutNav	OutNavTag	Inp1_Label	HasInp1	UseInp1	Inp1Offset	HasNav.0	NavTag[0]	Inp2_Label	HasInp2	UseInp2	Inp2Offset	HasNav.1	NavTag[1]	Inp3_Label	HasInp3	UseInp3	Inp3Offset	HasNav.2	NavTag[2]	Inp4_Label	HasInp4	UseInp4	Inp4Offset	HasNav.3	NavTag[3]	Inp5_Label	HasInp5	UseInp5	Inp5Offset	HasNav.4	NavTag[4]	Inp6_Label	HasInp6	UseInp6	Inp6Offset	HasNav.5	NavTag[5]
		Default Values:	0	High or Low Selector	High/Low Select	P_HiLoSel	area01	%	0	0	100	2	0	0		Input Inp 1	1	1	0	0		Input Inp 2	1	1	0	0		Input Inp 3	1	1	0	0		Input Inp 4	1	1	0	0		Input Inp 5	1	1	0	0		Input Inp 6	1	1	0	0
		MyP_HiLoSel	1	High or Low Selector	High/Low Select	P_HiLoSel	area01	%	1	0	100	2	0	0		Input 1	1	1	0	0		Input 2	1	1	0	0		Input 3	0	0	0	0		Input 4	0	0	0	0		Input 5	0	0	0	0		Input 6	0	0	0	0
			2
			3
			4
			5
			6
			7
			8
			9
			10
			11
			12
			13
			14
			15
			16
			17
			18
			19
			20
			21
			22
			23
			24
			25
			26
			27
			28
			29
			30	Strings too long to fit are formatted like this.
			31
			32
			33
			34
			35
			36
			37
			38
			39
			40
			41
			42
			43
			44
			45
			46
			47
			48
			49
			50

## P_Intlk
	P_Intlk: Interlocks with First-Out	Read From CLX:
		Send To CLX:

		Description:		Description for display on HMI	Label for graphic symbol displayed on HMI	Tagname for display on HMI	Process Area for security	1=Tells HMI an object with more info is available	Short HMI description of Interlock Condition 0	Bit indicates which state (0 or 1) of Inp_Intlk00 is OK to run	1=Interlock 00 is latched (requires reset)	Set bits indicate which conditions can be bypassed	Tagname for destinations of Navigation button 0	1=Enable Navigation Button 0	Short HMI description of Interlock Condition 1	Bit indicates which state (0 or 1) of Inp_Intlk01 is OK to run	1=Interlock 01 is latched (requires reset)	Set bits indicate which conditions can be bypassed	Tagname for destinations of Navigation button 1	1=Enable Navigation Button 1	Short HMI description of Interlock Condition 2	Bit indicates which state (0 or 1) of Inp_Intlk02 is OK to run	1=Interlock 02 is latched (requires reset)	Set bits indicate which conditions can be bypassed	Tagname for destinations of Navigation button 2	1=Enable Navigation Button 2	Short HMI description of Interlock Condition 3	Bit indicates which state (0 or 1) of Inp_Intlk03 is OK to run	1=Interlock 03 is latched (requires reset)	Set bits indicate which conditions can be bypassed	Tagname for destinations of Navigation button 3	1=Enable Navigation Button 3	Short HMI description of Interlock Condition 4	Bit indicates which state (0 or 1) of Inp_Intlk04 is OK to run	1=Interlock 04 is latched (requires reset)	Set bits indicate which conditions can be bypassed	Tagname for destinations of Navigation button 4	1=Enable Navigation Button 4	Short HMI description of Interlock Condition 5	Bit indicates which state (0 or 1) of Inp_Intlk05 is OK to run	1=Interlock 05 is latched (requires reset)	Set bits indicate which conditions can be bypassed	Tagname for destinations of Navigation button 5	1=Enable Navigation Button 5	Short HMI description of Interlock Condition 6	Bit indicates which state (0 or 1) of Inp_Intlk06 is OK to run	1=Interlock 06 is latched (requires reset)	Set bits indicate which conditions can be bypassed	Tagname for destinations of Navigation button 6	1=Enable Navigation Button 6	Short HMI description of Interlock Condition 7	Bit indicates which state (0 or 1) of Inp_Intlk07 is OK to run	1=Interlock 07 is latched (requires reset)	Set bits indicate which conditions can be bypassed	Tagname for destinations of Navigation button 7	1=Enable Navigation Button 7	Short HMI description of Interlock Condition 8	Bit indicates which state (0 or 1) of Inp_Intlk08 is OK to run	1=Interlock 08 is latched (requires reset)	Set bits indicate which conditions can be bypassed	Tagname for destinations of Navigation button 8	1=Enable Navigation Button 8	Short HMI description of Interlock Condition 9	Bit indicates which state (0 or 1) of Inp_Intlk09 is OK to run	1=Interlock 09 is latched (requires reset)	Set bits indicate which conditions can be bypassed	Tagname for destinations of Navigation button 9	1=Enable Navigation Button 9	Short HMI description of Interlock Condition 10	Bit indicates which state (0 or 1) of Inp_Intlk10 is OK to run	1=Interlock 10 is latched (requires reset)	Set bits indicate which conditions can be bypassed	Tagname for destinations of Navigation button 10	1=Enable Navigation Button 10	Short HMI description of Interlock Condition 11	Bit indicates which state (0 or 1) of Inp_Intlk11 is OK to run	1=Interlock 11 is latched (requires reset)	Set bits indicate which conditions can be bypassed	Tagname for destinations of Navigation button 11	1=Enable Navigation Button 11	Short HMI description of Interlock Condition 12	Bit indicates which state (0 or 1) of Inp_Intlk12 is OK to run	1=Interlock 12 is latched (requires reset)	Set bits indicate which conditions can be bypassed	Tagname for destinations of Navigation button 12	1=Enable Navigation Button 12	Short HMI description of Interlock Condition 13	Bit indicates which state (0 or 1) of Inp_Intlk13 is OK to run	1=Interlock 13 is latched (requires reset)	Set bits indicate which conditions can be bypassed	Tagname for destinations of Navigation button 13	1=Enable Navigation Button 13	Short HMI description of Interlock Condition 14	Bit indicates which state (0 or 1) of Inp_Intlk14 is OK to run	1=Interlock 14 is latched (requires reset)	Set bits indicate which conditions can be bypassed	Tagname for destinations of Navigation button 14	1=Enable Navigation Button 14	Short HMI description of Interlock Condition 15	Bit indicates which state (0 or 1) of Inp_Intlk15 is OK to run	1=Interlock 15 is latched (requires reset)	Set bits indicate which conditions can be bypassed	Tagname for destinations of Navigation button 15	1=Enable Navigation Button 15
		Usage:		Local	Local	Local	Local	Input	Local	Input	Input	Input	Local	Input	Local	Input	Input	Input	Local	Input	Local	Input	Input	Input	Local	Input	Local	Input	Input	Input	Local	Input	Local	Input	Input	Input	Local	Input	Local	Input	Input	Input	Local	Input	Local	Input	Input	Input	Local	Input	Local	Input	Input	Input	Local	Input	Local	Input	Input	Input	Local	Input	Local	Input	Input	Input	Local	Input	Local	Input	Input	Input	Local	Input	Local	Input	Input	Input	Local	Input	Local	Input	Input	Input	Local	Input	Local	Input	Input	Input	Local	Input	Local	Input	Input	Input	Local	Input	Local	Input	Input	Input	Local	Input
		Data Type:		STRING_40	STRING_20	STRING_20	STRING_Area	BOOL	STRING_Cond	BIT	BIT	BIT	STRING_NavTag	BIT	STRING_Cond	BIT	BIT	BIT	STRING_NavTag	BIT	STRING_Cond	BIT	BIT	BIT	STRING_NavTag	BIT	STRING_Cond	BIT	BIT	BIT	STRING_NavTag	BIT	STRING_Cond	BIT	BIT	BIT	STRING_NavTag	BIT	STRING_Cond	BIT	BIT	BIT	STRING_NavTag	BIT	STRING_Cond	BIT	BIT	BIT	STRING_NavTag	BIT	STRING_Cond	BIT	BIT	BIT	STRING_NavTag	BIT	STRING_Cond	BIT	BIT	BIT	STRING_NavTag	BIT	STRING_Cond	BIT	BIT	BIT	STRING_NavTag	BIT	STRING_Cond	BIT	BIT	BIT	STRING_NavTag	BIT	STRING_Cond	BIT	BIT	BIT	STRING_NavTag	BIT	STRING_Cond	BIT	BIT	BIT	STRING_NavTag	BIT	STRING_Cond	BIT	BIT	BIT	STRING_NavTag	BIT	STRING_Cond	BIT	BIT	BIT	STRING_NavTag	BIT	STRING_Cond	BIT	BIT	BIT	STRING_NavTag	BIT
			(Origin)	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_
Unit	Tag Description	TagName	Instance	Desc	Label	Tag	Area	HasMoreObj	CondTxt[0]	OKState.0	Latched.0	Bypassable.0	NavTag[0]	HasNav.0	CondTxt[1]	OKState.1	Latched.1	Bypassable.1	NavTag[1]	HasNav.1	CondTxt[2]	OKState.2	Latched.2	Bypassable.2	NavTag[2]	HasNav.2	CondTxt[3]	OKState.3	Latched.3	Bypassable.3	NavTag[3]	HasNav.3	CondTxt[4]	OKState.4	Latched.4	Bypassable.4	NavTag[4]	HasNav.4	CondTxt[5]	OKState.5	Latched.5	Bypassable.5	NavTag[5]	HasNav.5	CondTxt[6]	OKState.6	Latched.6	Bypassable.6	NavTag[6]	HasNav.6	CondTxt[7]	OKState.7	Latched.7	Bypassable.7	NavTag[7]	HasNav.7	CondTxt[8]	OKState.8	Latched.8	Bypassable.8	NavTag[8]	HasNav.8	CondTxt[9]	OKState.9	Latched.9	Bypassable.9	NavTag[9]	HasNav.9	CondTxt[10]	OKState.10	Latched.10	Bypassable.10	NavTag[10]	HasNav.10	CondTxt[11]	OKState.11	Latched.11	Bypassable.11	NavTag[11]	HasNav.11	CondTxt[12]	OKState.12	Latched.12	Bypassable.12	NavTag[12]	HasNav.12	CondTxt[13]	OKState.13	Latched.13	Bypassable.13	NavTag[13]	HasNav.13	CondTxt[14]	OKState.14	Latched.14	Bypassable.14	NavTag[14]	HasNav.14	CondTxt[15]	OKState.15	Latched.15	Bypassable.15	NavTag[15]	HasNav.15
		Default Values:	0	Interlocks with First Out	Interlocks	P_Intlk	area01	0	Enter Description #0	0	0	0		0		0	0	0		0		0	0	0		0		0	0	0		0		0	0	0		0		0	0	0		0		0	0	0		0		0	0	0		0		0	0	0		0		0	0	0		0		0	0	0		0		0	0	0		0		0	0	0		0		0	0	0		0		0	0	0		0		0	0	0		0
		AS_02_Intlk	1	Interlock Used for testing	P101 Interlocks	P_Intlk	area01	0	Enter Description #0	0	1	1		0		0	1	1		0		0	1	0		0		0	1	0		0		0	0	1		0		0	0	1		0		0	0	0		0		0	0	0		0		0	0	0		0		0	0	0		0		0	0	0		0		0	0	0		0		0	0	0		0		0	0	0		0		0	0	0		0		0	0	0		0
			2
			3
			4
			5
			6
			7
			8
			9
			10
			11
			12
			13
			14
			15
			16
			17
			18
			19
			20
			21
			22
			23
			24
			25
			26
			27
			28
			29
			30	Strings too long to fit are formatted like this.
			31
			32
			33
			34
			35
			36
			37
			38
			39
			40
			41
			42
			43
			44
			45
			46
			47
			48
			49
			50
			51
			52
			53
			54
			55
			56
			57
			58
			59
			60
			61
			62
			63
			64
			65
			66
			67
			68
			69
			70
			71
			72
			73
			74
			75
			76
			77
			78
			79
			80
			81
			82
			83
			84
			85
			86
			87
			88
			89
			90
			91
			92
			93
			94
			95
			96
			97
			98
			99

## P_IntlkAdv
	P_IntlkAdv: Advanced Interlocks with First-Out	Read From CLX:
		Send To CLX:

		Description:		Description for display on HMI	Label for graphic symbol displayed on HMI	Tagname for display on HMI	Process Area for security	Enable Selection for Types from HMI	1=Tells HMI an object with more info is available	Short HMI description of Interlock Condition 0	Type of Interlock 0	Bit indicates which state (0 or 1) of Inp_Intlk00 is OK to run	1=Interlock 00 is latched (requires reset)	Set bits indicate which conditions can be bypassed	Tagname for destinations of Navigation button 0	1=Enable Navigation Button 0	Short HMI description of Interlock Condition 1	Type of Interlock 1	Bit indicates which state (0 or 1) of Inp_Intlk01 is OK to run	1=Interlock 01 is latched (requires reset)	Set bits indicate which conditions can be bypassed	Tagname for destinations of Navigation button 1	1=Enable Navigation Button 1	Short HMI description of Interlock Condition 2	Type of Interlock 2	Bit indicates which state (0 or 1) of Inp_Intlk02 is OK to run	1=Interlock 02 is latched (requires reset)	Set bits indicate which conditions can be bypassed	Tagname for destinations of Navigation button 2	1=Enable Navigation Button 2	Short HMI description of Interlock Condition 3	Type of Interlock 3	Bit indicates which state (0 or 1) of Inp_Intlk03 is OK to run	1=Interlock 03 is latched (requires reset)	Set bits indicate which conditions can be bypassed	Tagname for destinations of Navigation button 3	1=Enable Navigation Button 3	Short HMI description of Interlock Condition 4	Type of Interlock 4	Bit indicates which state (0 or 1) of Inp_Intlk04 is OK to run	1=Interlock 04 is latched (requires reset)	Set bits indicate which conditions can be bypassed	Tagname for destinations of Navigation button 4	1=Enable Navigation Button 4	Short HMI description of Interlock Condition 5	Type of Interlock 5	Bit indicates which state (0 or 1) of Inp_Intlk05 is OK to run	1=Interlock 05 is latched (requires reset)	Set bits indicate which conditions can be bypassed	Tagname for destinations of Navigation button 5	1=Enable Navigation Button 5	Short HMI description of Interlock Condition 6	Type of Interlock 6	Bit indicates which state (0 or 1) of Inp_Intlk06 is OK to run	1=Interlock 06 is latched (requires reset)	Set bits indicate which conditions can be bypassed	Tagname for destinations of Navigation button 6	1=Enable Navigation Button 6	Short HMI description of Interlock Condition 7	Type of Interlock 7	Bit indicates which state (0 or 1) of Inp_Intlk07 is OK to run	1=Interlock 07 is latched (requires reset)	Set bits indicate which conditions can be bypassed	Tagname for destinations of Navigation button 7	1=Enable Navigation Button 7	Short HMI description of Interlock Condition 8	Type of Interlock 8	Bit indicates which state (0 or 1) of Inp_Intlk08 is OK to run	1=Interlock 08 is latched (requires reset)	Set bits indicate which conditions can be bypassed	Tagname for destinations of Navigation button 8	1=Enable Navigation Button 8	Short HMI description of Interlock Condition 9	Type of Interlock 9	Bit indicates which state (0 or 1) of Inp_Intlk09 is OK to run	1=Interlock 09 is latched (requires reset)	Set bits indicate which conditions can be bypassed	Tagname for destinations of Navigation button 9	1=Enable Navigation Button 9	Short HMI description of Interlock Condition 10	Type of Interlock 10	Bit indicates which state (0 or 1) of Inp_Intlk10 is OK to run	1=Interlock 10 is latched (requires reset)	Set bits indicate which conditions can be bypassed	Tagname for destinations of Navigation button 10	1=Enable Navigation Button 10	Short HMI description of Interlock Condition 11	Type of Interlock 11	Bit indicates which state (0 or 1) of Inp_Intlk11 is OK to run	1=Interlock 11 is latched (requires reset)	Set bits indicate which conditions can be bypassed	Tagname for destinations of Navigation button 11	1=Enable Navigation Button 11	Short HMI description of Interlock Condition 12	Type of Interlock 12	Bit indicates which state (0 or 1) of Inp_Intlk12 is OK to run	1=Interlock 12 is latched (requires reset)	Set bits indicate which conditions can be bypassed	Tagname for destinations of Navigation button 12	1=Enable Navigation Button 12	Short HMI description of Interlock Condition 13	Type of Interlock 13	Bit indicates which state (0 or 1) of Inp_Intlk13 is OK to run	1=Interlock 13 is latched (requires reset)	Set bits indicate which conditions can be bypassed	Tagname for destinations of Navigation button 13	1=Enable Navigation Button 13	Short HMI description of Interlock Condition 14	Type of Interlock 14	Bit indicates which state (0 or 1) of Inp_Intlk14 is OK to run	1=Interlock 14 is latched (requires reset)	Set bits indicate which conditions can be bypassed	Tagname for destinations of Navigation button 14	1=Enable Navigation Button 14	Short HMI description of Interlock Condition 15	Type of Interlock 15	Bit indicates which state (0 or 1) of Inp_Intlk15 is OK to run	1=Interlock 15 is latched (requires reset)	Set bits indicate which conditions can be bypassed	Tagname for destinations of Navigation button 15	1=Enable Navigation Button 15	Dispay Names for the Interlock Types	Dispay Names for the Interlock Types	Dispay Names for the Interlock Types	Dispay Names for the Interlock Types	Dispay Names for the Interlock Types	Dispay Names for the Interlock Types	Dispay Names for the Interlock Types	Dispay Names for the Interlock Types
		Usage:		Local	Local	Local	Local	Input	Input	Local	Input	Input	Input	Input	Local	Input	Local	Input	Input	Input	Input	Local	Input	Local	Input	Input	Input	Input	Local	Input	Local	Input	Input	Input	Input	Local	Input	Local	Input	Input	Input	Input	Local	Input	Local	Input	Input	Input	Input	Local	Input	Local	Input	Input	Input	Input	Local	Input	Local	Input	Input	Input	Input	Local	Input	Local	Input	Input	Input	Input	Local	Input	Local	Input	Input	Input	Input	Local	Input	Local	Input	Input	Input	Input	Local	Input	Local	Input	Input	Input	Input	Local	Input	Local	Input	Input	Input	Input	Local	Input	Local	Input	Input	Input	Input	Local	Input	Local	Input	Input	Input	Input	Local	Input	Local	Input	Input	Input	Input	Local	Input	Local	Local	Local	Local	Local	Local	Local	Local
		Data Type:		STRING_40	STRING_20	STRING_20	STRING_Area	SINT	BOOL	STRING_Cond	SINT	BIT	BIT	BIT	STRING_NavTag	BIT	STRING_Cond	SINT	BIT	BIT	BIT	STRING_NavTag	BIT	STRING_Cond	SINT	BIT	BIT	BIT	STRING_NavTag	BIT	STRING_Cond	SINT	BIT	BIT	BIT	STRING_NavTag	BIT	STRING_Cond	SINT	BIT	BIT	BIT	STRING_NavTag	BIT	STRING_Cond	SINT	BIT	BIT	BIT	STRING_NavTag	BIT	STRING_Cond	SINT	BIT	BIT	BIT	STRING_NavTag	BIT	STRING_Cond	SINT	BIT	BIT	BIT	STRING_NavTag	BIT	STRING_Cond	SINT	BIT	BIT	BIT	STRING_NavTag	BIT	STRING_Cond	SINT	BIT	BIT	BIT	STRING_NavTag	BIT	STRING_Cond	SINT	BIT	BIT	BIT	STRING_NavTag	BIT	STRING_Cond	SINT	BIT	BIT	BIT	STRING_NavTag	BIT	STRING_Cond	SINT	BIT	BIT	BIT	STRING_NavTag	BIT	STRING_Cond	SINT	BIT	BIT	BIT	STRING_NavTag	BIT	STRING_Cond	SINT	BIT	BIT	BIT	STRING_NavTag	BIT	STRING_Cond	SINT	BIT	BIT	BIT	STRING_NavTag	BIT	STRING_16	STRING_16	STRING_16	STRING_16	STRING_16	STRING_16	STRING_16	STRING_16
			(Origin)	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_
Unit	Tag Description	TagName	Instance	Desc	Label	Tag	Area	HasType	HasMoreObj	CondTxt[0]	Type0	OKState.0	Latched.0	Bypassable.0	NavTag[0]	HasNav.0	CondTxt[1]	Type1	OKState.1	Latched.1	Bypassable.1	NavTag[1]	HasNav.1	CondTxt[2]	Type2	OKState.2	Latched.2	Bypassable.2	NavTag[2]	HasNav.2	CondTxt[3]	Type3	OKState.3	Latched.3	Bypassable.3	NavTag[3]	HasNav.3	CondTxt[4]	Type4	OKState.4	Latched.4	Bypassable.4	NavTag[4]	HasNav.4	CondTxt[5]	Type5	OKState.5	Latched.5	Bypassable.5	NavTag[5]	HasNav.5	CondTxt[6]	Type6	OKState.6	Latched.6	Bypassable.6	NavTag[6]	HasNav.6	CondTxt[7]	Type7	OKState.7	Latched.7	Bypassable.7	NavTag[7]	HasNav.7	CondTxt[8]	Type8	OKState.8	Latched.8	Bypassable.8	NavTag[8]	HasNav.8	CondTxt[9]	Type9	OKState.9	Latched.9	Bypassable.9	NavTag[9]	HasNav.9	CondTxt[10]	Type10	OKState.10	Latched.10	Bypassable.10	NavTag[10]	HasNav.10	CondTxt[11]	Type11	OKState.11	Latched.11	Bypassable.11	NavTag[11]	HasNav.11	CondTxt[12]	Type12	OKState.12	Latched.12	Bypassable.12	NavTag[12]	HasNav.12	CondTxt[13]	Type13	OKState.13	Latched.13	Bypassable.13	NavTag[13]	HasNav.13	CondTxt[14]	Type14	OKState.14	Latched.14	Bypassable.14	NavTag[14]	HasNav.14	CondTxt[15]	Type15	OKState.15	Latched.15	Bypassable.15	NavTag[15]	HasNav.15	TypeDesc[0]	TypeDesc[1]	TypeDesc[2]	TypeDesc[3]	TypeDesc[4]	TypeDesc[5]	TypeDesc[6]	TypeDesc[7]
		Default Values:	0	Advanced Interlocks with First Out	Interlocks	P_Intlk	area01	-1	0	Enter Description #0	6	0	0	0		0		6	0	0	0		0		6	0	0	0		0		6	0	0	0		0		6	0	0	0		0		6	0	0	0		0		6	0	0	0		0		6	0	0	0		0		6	0	0	0		0		6	0	0	0		0		6	0	0	0		0		6	0	0	0		0		6	0	0	0		0		6	0	0	0		0		6	0	0	0		0		6	0	0	0		0	'Sft:Safety'	'Prt:Protective'	'Ele:Electrical'	'Dvc:Device'	'Opr:Operational'	'Mec:Mechanical'	'Gen:General'	'Pro:Process'
		MyP_IntlkAdv	1	Advanced Interlocks with First Out	P101 Interlocks	P_IntlkAdv	area01	-1	0	Enter Description #0	6	0	1	1		0		6	0	1	1		0		6	0	1	0		0		6	0	1	0		0		6	0	0	1		0		6	0	0	1		0		6	0	0	0		0		6	0	0	0		0		6	0	0	0		0		6	0	0	0		0		6	0	0	0		0		6	0	0	0		0		6	0	0	0		0		6	0	0	0		0		6	0	0	0		0		6	0	0	0		0	'Sft:Safety'	'Prt:Protective'	'Ele:Electrical'	'Dvc:Device'	'Opr:Operational'	'Mec:Mechanical'	'Gen:General'	'Pro:Process'
			2
			3
			4
			5
			6
			7
			8
			9
			10
			11
			12
			13
			14
			15
			16
			17
			18
			19
			20
			21
			22
			23
			24
			25
			26
			27
			28
			29
			30	Strings too long to fit are formatted like this.
			31
			32
			33
			34
			35
			36
			37
			38
			39
			40
			41
			42
			43
			44
			45
			46
			47
			48
			49
			50
			51
			52
			53
			54
			55
			56
			57
			58
			59
			60
			61
			62
			63
			64
			65
			66
			67
			68
			69
			70
			71
			72
			73
			74
			75
			76
			77
			78
			79
			80
			81
			82
			83
			84
			85
			86
			87
			88
			89
			90
			91
			92
			93
			94
			95
			96
			97
			98
			99

## P_LLS
	P_LLS: Lead / Lag / Standby Motor Group	Read From CLX:
		Send To CLX:

		Description:		Description for display on HMI	Label for graphic symbol displayed on HMI	Tagname for display on HMI	Process Area for security	Number of motors in this Lead / Lag / Standby Group (2..30)	Maximum number of motors to run (1..NumMotors)	Minimum number of motors to run (0..MaxDemand)	Time (sec) after start or stop until next start is allowed (0..2M sec)	Time (sec) after start or stop until next stop is allowed (0..2M sec)	1=First started is first stopped, 0=First started is last stopped	1=Allow Rotate ("cycle lead") command to rotate motor assignments	1=Rotate (cycle lead to end of list) upon stopping all motors	1=Tells HMI a P_Perm is connected to Inp_Perm	1=Tells HMI a P_Intlk is connected to Inp_Intlk	1=Tells HMI an object with more info is available	1=Motor Navigation button is enabled	1=Motor Navigation button is enabled	1=Motor Navigation button is enabled	1=Motor Navigation button is enabled	1=Motor Navigation button is enabled	1=Motor Navigation button is enabled	1=Motor Navigation button is enabled	1=Motor Navigation button is enabled	Cant Start Alarm Condition	Cant Start Alarm Tag	1=Fail to Start Alarm exists and will be checked	1=Reset required to clear Fail to Start Alarm	1=Acknowledged required for Fail to Start Alarm	Fail to Start Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	Cant Stop Alarm Condition	Cant Stop Alarm Tag	1=Fail to Stop Alarm exists and will be checked	1=Reset required to clear Fail to Stop Alarm	Fail to Start Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	Fail to Stop Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	Interlock Tripped Alarm Condition	Interlock Tripped Alarm Tag	1=Interlock Trip Alarm exists and will be checked	1=Reset required to clear Interlock Trip Alarm	1=Interlock Tripped Alarm must be acknowledged	Interlock Trip Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	1=OCmd_Stop available in any mode, 0=OCmd_Stop only in Oper, Maint modes.	1=XCmd_Stop any time, 0=XCmd_Stop only when Ext selected	1=New Oper motor cmd. resets fault, 0=reset reqd to clear fault	1=New Device XCmd resets shed latches and cleared alarms, 0=OCmdReset reqd	1=Override ignores Bypassable Perm/ Intlk; 0=always use Perm/Intlk	1=PSets track OSets in Oper, OSets track PSets in Prog, 0=no tracking	1=Prog/Oper Settings track Override/Hand Peed reference	1=Operator (unlocked) exists, can be selected	1=Operator Locked exists, can be selected	1=Program (unlocked) exists, can be selected	1=Program Locked exists, can be selected	1=External exists, can be selected	1=Maintenance exists, can be selected	1=Maintenance Out of Service exists, can be selected	1=Override supersedes Prog/Oper Lock, 0=don't override Lock	1=External supersedes Prog/Oper Lock, 0=don't override Lock	1=Power Up to Prog, 0=Power Up to Oper	Normal Source: 1=Program if no requests; 0=Operator if no requests	Command Priority: 1=Program Cmds Win; 0=Operator Cmds Win	1=PCmd_Prog used as a Level (1=Prog, 0=Oper)	1=PCmd_Lock used as a Level (1=Lock, 0=Unlock)	1=XCmd_Acq used as Level (1=Acq, 0=Rel)
		Usage:		Local	Local	Local	Local	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Local	Local	Local	Local	Local	Local	Local	Local	Input	Input	Input	Input	Input	Input	Input	Local	Local	Local	Local	Local	Local	Local	Local
		Data Type:		STRING_40	STRING_20	STRING_20	STRING_Area	DINT	DINT	DINT	REAL	REAL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BIT	BIT	BIT	BIT	BIT	BIT	BIT	BIT	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL
			(Origin)	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.CantStart.Cfg_	.CantStart.Cfg_	.CantStart.Cfg_	.CantStart.Cfg_	.CantStart.Cfg_	.CantStart.Cfg_	.CantStart.Cfg_	.CantStart.Cfg_	.CantStop.Cfg_	.CantStop.Cfg_	.CantStop.Cfg_	.CantStop.Cfg_	.CantStop.Cfg_	.CantStop.Cfg_	.CantStop.Cfg_	.CantStop.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_
Unit	Tag Description	TagName	Instance	Desc	Label	Tag	Area	NumMotors	MaxDemand	MinDemand	StartDelay	StopDelay	FirstOnFirstOff	AllowRotate	RotateOnStop	HasPermObj	HasIntlkObj	HasMoreObj	HasNav.0	HasNav.1	HasNav.2	HasNav.3	HasNav.4	HasNav.5	HasNav.6	HasNav.7	HasNav.8	HasNav.9	HasNav.10	HasNav.11	HasNav.12	HasNav.13	HasNav.14	HasNav.15	HasNav.16	HasNav.17	HasNav.18	HasNav.19	HasNav.20	HasNav.21	HasNav.22	HasNav.23	HasNav.24	HasNav.25	HasNav.26	HasNav.27	HasNav.28	HasNav.29	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	OperStopPrio	ExtStopPrio	OCmdResets	XCmdResets	OvrdPermIntlk	SetTrack	SetTrackOvrdHand	HasOper	HasOperLocked	HasProg	HasProgLocked	HasExt	HasMaint	HasMOoS	OvrdOverLock	ExtOverLock	ProgPwrUp	ProgNormal	PCmdPriority	PCmdProgAsLevel	PCmdLockAsLevel	ExtAcqAsLevel
		Default Values:	0	Lead / Lag / Standby Motor Group	Motor Group Control	P_LLS	area01	3	2	0	10	10	0	1	1	0	0	0	0	0	0	0	0	Cant Start	XAR-nnnn	0	0	1	1000	0	1	5	480	Failed to Stop	XAS-nnnnA	0	0	1	1000	0	1	5	480	Interlock Trip	XAS-nnnnB	0	0	1	500	0	1	5	480	0	0	0	0	0	1	0	1	1	1	1	0	1	1	1	0	0	0	0	0	0	0
		MyP_LLS	1	Lead / Lag / Standby Motor Group	Motor Group Control	P_LLS	area01	4	3	0	10	10	0	1	0	0	0	0	1	1	1	1	0	0	0	0	0	0	0	0	No motors to start	Alarm Tag 1234567890	0	0	1	750	1	1	5	480	No motors to stop	Alarm Tag 1234567890	0	0	1	750	1	1	5	480	Interlock Trip	Alarm Tag 1234567890	0	0	1	500	1	1	5	480	0	0	0	0	0	1	0	1	1	1	1	0	1	1	1	0	0	0	0	0	0	0
			2
			3
			4
			5
			6
			7
			8
			9
			10
			11
			12
			13
			14
			15
			16
			17
			18
			19
			20
			21
			22
			23
			24
			25
			26
			27
			28
			29
			30	Strings too long to fit are formatted like this.
			31
			32
			33
			34
			35
			36
			37
			38
			39
			40
			41
			42
			43
			44
			45
			46
			47
			48
			49
			50
			51
			52
			53
			54
			55
			56
			57
			58
			59
			60
			61
			62
			63
			64
			65
			66
			67
			68
			69
			70
			71
			72
			73
			74
			75
			76
			77
			78
			79
			80
			81
			82
			83
			84
			85
			86
			87
			88
			89
			90
			91
			92
			93
			94
			95
			96
			97
			98
			99

## P_Logic
	P_Logic: Boolean Logic	Read From CLX:
		Send To CLX:

		Description:		Description for display on HMI	Label for graphic symbol displayed on HMI	Tagname for display on HMI	Process Area for security	Text to display in Out=0 State	Text to display in Out=1 State	Output OFF delay time (sec)	Output ON delay time (sec)	Out Source (before Min Duration Timer) is Inverted (1=invert)	Source bit for Output (0..7 = inputs, 8..15 = gates)	1=New snapshot overwrites without reset, 0=save first snapshot till reset	1=Generate a TimeStamp when Snapshot occurs	1=Use Inp_Hold to snap state; 0=Use Cmds or Output transition to snap	1=Enable snapshot on PCmd_Snap 0 --> 1 (edge)	1=Enable snapshot on OCmd_Snap 0 --> 1 (edge)	1=Enable snapshot on Output 0 --> 1 (rising edge)	1=Enable snapshot on Output 1 --> 0 (falling edge)	1=Tells HMI an object with more info is available	Short HMI description of Input 0	1=Enable Navigation button for Input 0	Tagname for destination of Input 0 Navigation button	Short HMI description of Input 1	1=Enable Navigation button for Input 1	Tagname for destination of Input 1 Navigation button	Short HMI description of Input 2	1=Enable Navigation button for Input 2	Tagname for destination of Input 2 Navigation button	Short HMI description of Input 3	1=Enable Navigation button for Input 3	Tagname for destination of Input 3 Navigation button	Short HMI description of Input 4	1=Enable Navigation button for Input 4	Tagname for destination of Input 4 Navigation button	Short HMI description of Input 5	1=Enable Navigation button for Input 5	Tagname for destination of Input 5 Navigation button	Short HMI description of Input 6	1=Enable Navigation button for Input 6	Tagname for destination of Input 6 Navigation button	Short HMI description of Input 7	1=Enable Navigation button for Input 7	Tagname for destination of Input 7 Navigation button	Function code for Gate 0 (1=AND, 2=OR, 3=XOR, 4=2oo3, 5=Set-Reset)	Gate M Source #1 is Used (M by bit) (1=used)	Gate M Source #1 is Inverted (M by bit) (1=invert)	Pointer to Gate 0 Source #1 (0..7 = inputs, 8..15 = gate outputs)	Gate M Source #2 is Used (M by bit) (1=used)	Gate M Source #2 is Inverted (M by bit) (1=invert)	Pointer to Gate 0 Source #2 (0..7 = inputs, 8..15 = gate outputs)	Gate M Source #3 is Used (M by bit) (1=used)	Gate M Source #3 is Inverted (M by bit) (1=invert)	Pointer to Gate 0 Source #3 (0..7 = inputs, 8..15 = gate outputs)	Gate M Source #4 is Used (M by bit) (1=used)	Gate M Source #4 is Inverted (M by bit) (1=invert)	Pointer to Gate 0 Source #4 (0..7 = inputs, 8..15 = gate outputs)	Function code for Gate 1 (1=AND, 2=OR, 3=XOR, 4=2oo3, 5=Set-Reset)	Gate 1 Source #1 is Used (1=used)	Gate 1 Source #1 is Inverted (1=invert)	Pointer to Gate 1 Source #1 (0..7 = inputs, 8..15 = gate outputs)	Gate 1 Source #2 is Used (1=used)	Gate 1 Source #2 is Inverted (1=invert)	Pointer to Gate 1 Source #2 (0..7 = inputs, 8..15 = gate outputs)	Gate 1 Source #3 is Used (1=used)	Gate 1 Source #3 is Inverted (1=invert)	Pointer to Gate 1 Source #3 (0..7 = inputs, 8..15 = gate outputs)	Gate 1 Source #4 is Used (1=used)	Gate 1 Source #4 is Inverted (1=invert)	Pointer to Gate 1 Source #4 (0..7 = inputs, 8..15 = gate outputs)	Function code for Gate 1 (1=AND, 2=OR, 3=XOR, 4=2oo3, 5=Set-Reset)	Gate 1 Source #1 is Used (1=used)	Gate 1 Source #1 is Inverted (1=invert)	Pointer to Gate 1 Source #1 (0..7 = inputs, 8..15 = gate outputs)	Gate 1 Source #2 is Used (1=used)	Gate 1 Source #2 is Inverted (1=invert)	Pointer to Gate 1 Source #2 (0..7 = inputs, 8..15 = gate outputs)	Gate 1 Source #3 is Used (1=used)	Gate 1 Source #3 is Inverted (1=invert)	Pointer to Gate 1 Source #3 (0..7 = inputs, 8..15 = gate outputs)	Gate 1 Source #4 is Used (1=used)	Gate 1 Source #4 is Inverted (1=invert)	Pointer to Gate 1 Source #4 (0..7 = inputs, 8..15 = gate outputs)	Function code for Gate 3 (1=AND, 2=OR, 3=XOR, 4=2oo3, 5=Set-Reset)	Gate 3 Source #1 is Used (1=used)	Gate 3 Source #1 is Inverted (1=invert)	Pointer to Gate 3 Source #1 (0..7 = inputs, 8..15 = gate outputs)	Gate 3 Source #2 is Used (1=used)	Gate 3 Source #2 is Inverted (1=invert)	Pointer to Gate 3 Source #2 (0..7 = inputs, 8..15 = gate outputs)	Gate 3 Source #3 is Used (1=used)	Gate 3 Source #3 is Inverted (1=invert)	Pointer to Gate 3 Source #3 (0..7 = inputs, 8..15 = gate outputs)	Gate 3 Source #4 is Used (1=used)	Gate 3 Source #4 is Inverted (1=invert)	Pointer to Gate 3 Source #4 (0..7 = inputs, 8..15 = gate outputs)	Function code for Gate 4 (1=AND, 2=OR, 3=XOR, 4=2oo3, 5=Set-Reset)	Gate 4 Source #1 is Used (1=used)	Gate 4 Source #1 is Inverted (1=invert)	Pointer to Gate 4 Source #1 (0..7 = inputs, 8..15 = gate outputs)	Gate 4 Source #2 is Used (1=used)	Gate 4 Source #2 is Inverted (1=invert)	Pointer to Gate 4 Source #2 (0..7 = inputs, 8..15 = gate outputs)	Gate 4 Source #3 is Used (1=used)	Gate 4 Source #3 is Inverted (1=invert)	Pointer to Gate 4 Source #3 (0..7 = inputs, 8..15 = gate outputs)	Gate 4 Source #4 is Used (1=used)	Gate 4 Source #4 is Inverted (1=invert)	Pointer to Gate 4 Source #4 (0..7 = inputs, 8..15 = gate outputs)	Function code for Gate 5 (1=AND, 2=OR, 3=XOR, 4=2oo3, 5=Set-Reset)	Gate 5 Source #1 is Used (1=used)	Gate 5 Source #1 is Inverted (1=invert)	Pointer to Gate 5 Source #1 (0..7 = inputs, 8..15 = gate outputs)	Gate 5 Source #2 is Used (1=used)	Gate 5 Source #2 is Inverted (1=invert)	Pointer to Gate 5 Source #2 (0..7 = inputs, 8..15 = gate outputs)	Gate 5 Source #3 is Used (1=used)	Gate 5 Source #3 is Inverted (1=invert)	Pointer to Gate 5 Source #3 (0..7 = inputs, 8..15 = gate outputs)	Gate 5 Source #4 is Used (1=used)	Gate 5 Source #4 is Inverted (1=invert)	Pointer to Gate 5 Source #4 (0..7 = inputs, 8..15 = gate outputs)	Function code for Gate 6 (1=AND, 2=OR, 3=XOR, 4=2oo3, 5=Set-Reset)	Gate 6 Source #1 is Used (1=used)	Gate 6 Source #1 is Inverted (1=invert)	Pointer to Gate 6 Source #1 (0..7 = inputs, 8..15 = gate outputs)	Gate 6 Source #2 is Used (1=used)	Gate 6 Source #2 is Inverted (1=invert)	Pointer to Gate 6 Source #2 (0..7 = inputs, 8..15 = gate outputs)	Gate 6 Source #3 is Used (1=used)	Gate 6 Source #3 is Inverted (1=invert)	Pointer to Gate 6 Source #3 (0..7 = inputs, 8..15 = gate outputs)	Gate 6 Source #4 is Used (1=used)	Gate 6 Source #4 is Inverted (1=invert)	Pointer to Gate 6 Source #4 (0..7 = inputs, 8..15 = gate outputs)	Function code for Gate 7 (1=AND, 2=OR, 3=XOR, 4=2oo3, 5=Set-Reset)	Gate 7 Source #1 is Used (1=used)	Gate 7 Source #1 is Inverted (1=invert)	Pointer to Gate 7 Source #1 (0..7 = inputs, 8..15 = gate outputs)	Gate 7 Source #2 is Used (1=used)	Gate 7 Source #2 is Inverted (1=invert)	Pointer to Gate 7 Source #2 (0..7 = inputs, 8..15 = gate outputs)	Gate 7 Source #3 is Used (1=used)	Gate 7 Source #3 is Inverted (1=invert)	Pointer to Gate 7 Source #3 (0..7 = inputs, 8..15 = gate outputs)	Gate 7 Source #4 is Used (1=used)	Gate 7 Source #4 is Inverted (1=invert)	Pointer to Gate 7 Source #4 (0..7 = inputs, 8..15 = gate outputs)
		Usage:		Local	Local	Local	Local	Local	Local	Input	Input	Local	Local	Input	Input	Input	Input	Input	Input	Input	Input	Local	Input	Local	Local	Input	Local	Local	Input	Local	Local	Input	Local	Local	Input	Local	Local	Input	Local	Local	Input	Local	Local	Input	Local	Local	Local	Local	Local	Local	Local	Local
		Data Type:		STRING_40	STRING_20	STRING_20	STRING_Area	STRING_8	STRING_8	REAL	REAL	BOOL	DINT	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	STRING_Cond	BOOL	STRING_NavTag	STRING_Cond	BOOL	STRING_NavTag	STRING_Cond	BOOL	STRING_NavTag	STRING_Cond	BOOL	STRING_NavTag	STRING_Cond	BOOL	STRING_NavTag	STRING_Cond	BOOL	STRING_NavTag	STRING_Cond	BOOL	STRING_NavTag	STRING_Cond	BOOL	STRING_NavTag	DINT	BOOL	BOOL	DINT	BOOL	BOOL	DINT	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	BOOL	BOOL	DINT	BOOL	BOOL	DINT	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	BOOL	BOOL	DINT	BOOL	BOOL	DINT	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	BOOL	BOOL	DINT	BOOL	BOOL	DINT	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	BOOL	BOOL	DINT	BOOL	BOOL	DINT	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	BOOL	BOOL	DINT	BOOL	BOOL	DINT	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	BOOL	BOOL	DINT	BOOL	BOOL	DINT	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	BOOL	BOOL	DINT	BOOL	BOOL	DINT	BOOL	BOOL	DINT	BOOL	BOOL	DINT
			(Origin)	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_
Unit	Tag Description	TagName	Instance	Desc	Label	Tag	Area	0StText	1StText	OffDelay	OnDelay	OutSrcInv	OutSrcPtr	SnapOver	TSonSnap	UseInpHold	UsePCmd	UseOCmd	UseOut01	UseOut10	HasMoreObj	InpTxt[0]	HasNav.0	NavTag[0]	InpTxt[1]	HasNav.1	NavTag[1]	InpTxt[2]	HasNav.2	NavTag[2]	InpTxt[3]	HasNav.3	NavTag[3]	InpTxt[4]	HasNav.4	NavTag[4]	InpTxt[5]	HasNav.5	NavTag[5]	InpTxt[6]	HasNav.6	NavTag[6]	InpTxt[7]	HasNav.7	NavTag[7]	GateFunc[0]	GateSrc1Mask.0	GateSrc1Inv.0	GateSrc1Ptr[0]	GateSrc2Mask.0	GateSrc2Inv.0	GateSrc2Ptr[0]	GateSrc3Mask.0	GateSrc3Inv.0	GateSrc3Ptr[0]	GateSrc4Mask.0	GateSrc4Inv.0	GateSrc4Ptr[0]	GateFunc[1]	GateSrc1Mask.1	GateSrc1Inv.1	GateSrc1Ptr[1]	GateSrc2Mask.1	GateSrc2Inv.1	GateSrc2Ptr[1]	GateSrc3Mask.1	GateSrc3Inv.1	GateSrc3Ptr[1]	GateSrc4Mask.1	GateSrc4Inv.1	GateSrc4Ptr[1]	GateFunc[2]	GateSrc1Mask.2	GateSrc1Inv.2	GateSrc1Ptr[2]	GateSrc2Mask.2	GateSrc2Inv.2	GateSrc2Ptr[2]	GateSrc3Mask.2	GateSrc3Inv.2	GateSrc3Ptr[2]	GateSrc4Mask.2	GateSrc4Inv.2	GateSrc4Ptr[2]	GateFunc[3]	GateSrc1Mask.3	GateSrc1Inv.3	GateSrc1Ptr[3]	GateSrc2Mask.3	GateSrc2Inv.3	GateSrc2Ptr[3]	GateSrc3Mask.3	GateSrc3Inv.3	GateSrc3Ptr[3]	GateSrc4Mask.3	GateSrc4Inv.3	GateSrc4Ptr[3]	GateFunc[4]	GateSrc1Mask.4	GateSrc1Inv.4	GateSrc1Ptr[4]	GateSrc2Mask.4	GateSrc2Inv.4	GateSrc2Ptr[4]	GateSrc3Mask.4	GateSrc3Inv.4	GateSrc3Ptr[4]	GateSrc4Mask.4	GateSrc4Inv.4	GateSrc4Ptr[4]	GateFunc[5]	GateSrc1Mask.5	GateSrc1Inv.5	GateSrc1Ptr[5]	GateSrc2Mask.5	GateSrc2Inv.5	GateSrc2Ptr[5]	GateSrc3Mask.5	GateSrc3Inv.5	GateSrc3Ptr[5]	GateSrc4Mask.5	GateSrc4Inv.5	GateSrc4Ptr[5]	GateFunc[6]	GateSrc1Mask.6	GateSrc1Inv.6	GateSrc1Ptr[6]	GateSrc2Mask.6	GateSrc2Inv.6	GateSrc2Ptr[6]	GateSrc3Mask.6	GateSrc3Inv.6	GateSrc3Ptr[6]	GateSrc4Mask.6	GateSrc4Inv.6	GateSrc4Ptr[6]	GateFunc[7]	GateSrc1Mask.7	GateSrc1Inv.7	GateSrc1Ptr[7]	GateSrc2Mask.7	GateSrc2Inv.7	GateSrc2Ptr[7]	GateSrc3Mask.7	GateSrc3Inv.7	GateSrc3Ptr[7]	GateSrc4Mask.7	GateSrc4Inv.7	GateSrc4Ptr[7]
		Default Values:	0	Configurable Boolean Logic Block	Configurable Logic	P_Logic	area01	OK	TRIPPED	0	0	0	0	0	0	0	1	1	1	0	0	Input Condition 0	0			0			0			0			0			0			0			0		0	0	0	0	0	0	0	0
		MyP_Logic	1	Loginator	Configurable Logic	P_Logic	area01	OK	TRIPPED	0	0	0	0	0	0	0	1	1	1	0	0	Vessel 1 Empty	0	MyDiscreteOut	Vessel 2 Empty	0		Vessel 3 Empty	0		Consumer 1 Short	0		Consumer 2 Short	0		Consumer 3 Short	0		Override State	0		Override Switch	0		0	0	0	0	0	0	0	0	4	1	0	0	1	0	1	0	0	0	1	0	2	0	0	0	0	0	0	0	0	2	1	0	3	0	0	0	1	0	4	1	0	5	0	0	0	0	0	0	0	0	1	1	0	9	0	0	0	0	0	0	1	0	11	0	0	0	0	0	0	0	0	6	1	0	13	1	0	6	1	0	7	0	0	0
			2
			3
			4
			5
			6
			7
			8
			9
			10
			11
			12
			13
			14
			15
			16
			17
			18
			19
			20
			21
			22
			23
			24
			25
			26
			27
			28
			29
			30	Strings too long to fit are formatted like this.
			31
			32
			33
			34
			35
			36
			37
			38
			39
			40
			41
			42
			43
			44
			45
			46
			47
			48
			49
			50
			51
			52
			53
			54
			55
			56
			57
			58
			59
			60
			61
			62
			63
			64
			65
			66
			67
			68
			69
			70
			71
			72
			73
			74
			75
			76
			77
			78
			79
			80
			81
			82
			83
			84
			85
			86
			87
			88
			89
			90
			91
			92
			93
			94
			95
			96
			97
			98
			99

## P_Motor
	P_Motor: Single Speed Motor	Read From CLX:
		Send To CLX:

		Description:		Description for display on HMI	Label for graphic symbol displayed on HMI	Tagname for display on HMI	Process Area for security	1=Allow Local Start/Stop without alarm, 0=Start/Stop from HMI/prog only	1=Motor provides run feedback	1=Motor run feedback should be used for failure checking	Time after Start to get Run Feedback before Fault (sec)	Time after Stop to drop Run Feedback before Fault (sec)	1=Stop Motor and Alarm on Fail to Start; 0=Alarm only on Fail to Start	1=Stop Motor and Alarm on I/O Fault; 0=Alarm only on I/O Fault	Delay to echo back of Running/Stopped status when in Simulation (sec)	1=Enable navigation to Permissive object	1=Enable navigation to Interlock object	1=Enable navigation to Restart Inhibit object	1=Enable navigation to Run Time object	1=Enable navigation to Overload object	1=Tells HMI an object with more info is available	1=Motor Jog Command enabled/visible, 0=Motor Jog Command not allowed	Maximum jog time (sec, 0=unlimited)	Time to sound audible on commanded start (sec) (0=disabled)	Fail To Start Alarm Condition	Fail To Start Alarm Tag	1=Fail To Start Alarm exists and will be checked	1=Reset required to clear Fail To Start Alarm	1=Acknowledge required for Fail To Start Alarm	Fail To Start Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	Fail To Stop Alarm Condition	Fail To Stop Alarm Tag	1=Fail To Stop Alarm exists and will be checked	1=Reset required to clear Fail To Stop Alarm	1=Acknowledge required for Fail To Stop Alarm	Fail To Stop Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	Interlock Tripped Alarm Condition	Interlock Tripped Alarm Tag	1=Interlock Tripped Alarm exists and will be checked	1=Reset required to clear Interlock Trip Alarm	1=Acknowledge required for Interlock Trip Alarm	Interlock Trip Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	I/O Fault Alarm Condition	I/O Fault Alarm Tag	1=I/O Fault Alarm exists and will be checked	1=Reset required to clear I/O Fault Alarm	1=Acknowledge required for I/O Fault Alarm	I/O Fault Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	1=OCmd_Stop any time, 0=OCmd_Stop only when Oper selected	1=XCmd_Stop any time, 0=XCmd_Stop only when Ext selected	1=New motor OCmd resets shed latches and cleared alarms, 0=OCmdReset reqd	1=New Device XCmd resets shed latches and cleared alarms, 0=XCmdReset reqd	1=Override ignores Bypassable Perm/ Intlk; 0=always use Perm/Intlk	1=Operator (unlocked) exists, can be selected	1=Operator Locked exists, can be selected	1=Program (unlocked) exists, can be selected	1=Program Locked exists, can be selected	1=External exists, can be selected	1=Maintenance exists, can be selected	1=Maintenance Out of Service exists, can be selected	1=Override supersedes Prog/Oper Lock, 0=don't override Lock	1=External supersedes Prog/Oper Lock, 0=don't override Lock	1=Power Up to Prog, 0=Power Up to Oper	Normal Source: 1=Program if no requests; 0=Operator if no requests	Command Priority: 1=Program Cmds Win; 0=Operator Cmds Win	1=PCmd_Prog used as a Level (1=Prog, 0=Oper)	1=PCmd_Lock used as a Level (1=Lock, 0=Unlock)	1=XCmd_Acq used as Level (1=Acq, 0=Rel)
		Usage:		Local	Local	Local	Local	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Local	Local	Local	Local	Local	Local	Local	Local	Input	Input	Input	Input	Input	Local	Local	Local	Local	Local	Local	Local	Local
		Data Type:		STRING_40	STRING_20	STRING_20	STRING_Area	BOOL	BOOL	BOOL	REAL	REAL	BOOL	BOOL	REAL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	REAL	REAL	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL
			(Origin)	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.FailToStart.Cfg_	.FailToStart.Cfg_	.FailToStart.Cfg_	.FailToStart.Cfg_	.FailToStart.Cfg_	.FailToStart.Cfg_	.FailToStart.Cfg_	.FailToStart.Cfg_	.FailToStop.Cfg_	.FailToStop.Cfg_	.FailToStop.Cfg_	.FailToStop.Cfg_	.FailToStop.Cfg_	.FailToStop.Cfg_	.FailToStop.Cfg_	.FailToStop.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_
Unit	Tag Description	TagName	Instance	Desc	Label	Tag	Area	AllowLocal	HasRunFdbk	UseRunFdbk	FailToStartT	FailToStopT	ShedOnFailToStart	ShedOnIOFault	SimFdbkT	HasPermObj	HasIntlkObj	HasResInhObj	HasRunTimeObj	HasOvldObj	HasMoreObj	HasJog	MaxJogT	StartHornT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	OperStopPrio	ExtStopPrio	OCmdResets	XCmdResets	OvrdPermIntlk	HasOper	HasOperLocked	HasProg	HasProgLocked	HasExt	HasMaint	HasMOoS	OvrdOverLock	ExtOverLock	ProgPwrUp	ProgNormal	PCmdPriority	PCmdProgAsLevel	PCmdLockAsLevel	ExtAcqAsLevel
		Default Values:	0	Single Speed Motor	Motor Control	P_Motor	area01	0	0	0	10	10	1	1	2	0	0	0	0	0	0	0	0	0	Failed to Start	XAR-nnnn	0	0	1	1000	0	1	5	480	Failed to Stop	XAS-nnnnA	0	0	1	1000	0	1	5	480	Interlock Trip	XAS-nnnnB	0	0	1	500	0	1	5	480	I/O Fault	XAF-nnnn	0	0	1	1000	0	1	5	480	0	0	0	0	0	1	1	1	1	0	1	1	1	0	0	0	0	0	0	0
		MyP_Motor	1	Single Speed Motor	Motor Control	MyMotor	area01	0	1	1	10	10	1	1	15	0	1	1	1	1	0	0	0	0	Failed to Start	MyMotor.FailToStart	1	0	1	3	1	1	5	480	Failed to Stop	MyMotor.FailToStop	1	0	1	3	1	1	5	480	Interlock Trip	MyMotor.IntlkTrip	1	0	1	3	1	1	5	480	I/O Fault	MyMotor.IOFault	1	0	1	3	1	1	5	480	0	0	0	0	0	1	1	1	1	0	1	1	1	0	0	0	0	0	0	0
			2
			3
			4
			5
			6
			7
			8
			9
			10
			11
			12
			13
			14
			15
			16
			17
			18
			19
			20
			21
			22
			23
			24
			25
			26
			27
			28
			29
			30	Strings too long to fit are formatted like this.
			31
			32
			33
			34
			35
			36
			37
			38
			39
			40
			41
			42
			43
			44
			45
			46
			47
			48
			49
			50
			51
			52
			53
			54
			55
			56
			57
			58
			59
			60
			61
			62
			63
			64
			65
			66
			67
			68
			69
			70
			71
			72
			73
			74
			75
			76
			77
			78
			79
			80
			81
			82
			83
			84
			85
			86
			87
			88
			89
			90
			91
			92
			93
			94
			95
			96
			97
			98
			99

## P_Motor2Spd
	P_Motor2Spd: Two Speed Motor	Read From CLX:
		Send To CLX:

		Description:		Description for display on HMI	Label for graphic symbol displayed on HMI	Tagname for display on HMI	Process Area for security	Description for FAST speed	Description for SLOW speed	Delay with contactors open when changing speeds (sec)	1=Allow Local Start/Stop without alarm, 0=Start/Stop from HMI/prog only	1=Motor provides run feedbacks	1=Use motor run feedback for failure checking	Time after Start to get correct Run Feedback before Fault (sec)	Time after Stop to drop Run Feedbacks before Fault (sec)	1=Stop Motor and Alarm on Fail to Start; 0=Alarm only on Fail to Start	1=Stop Motor and Alarm on I/O Fault; 0=Alarm only on I/O Fault	Delay to echo back of Running/Stopped status when in Simulation (sec)	1=Tells HMI a P_Perm is connected to Inp_SlowPermOK	1=Tells HMI a P_Perm is connected to Inp_FastPermOK	1=Tells HMI a P_Intlk is connected to Inp_Intlk	1=Tell HMI a P_ResInh Restart Inhibit is connected	1=Tells HMI a P_RunTime is connected	1=Tell HMI an Overload object exists (E3+,etc.)	1=Tells HMI an object with more info is available	1=Motor Jog Command enabled/visible, 0=Motor Jog Command not allowed	Maximum jog time (sec, 0=unlimited)	Time to sound audible on commanded start (sec) (0=disabled)	Fail To Start Alarm Condition	Fail To Start Alarm Tag	1=Fail To Start Alarm exists and will be checked	1=Reset required to clear Fail To Start Alarm	1=Fail To Start Alarm must be acknowledged	Fail To Start Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	Fail To Stop Alarm Condition	Fail To Stop Alarm Tag	1=Fail To Stop Alarm exists and will be checked	1=Reset required to clear Fail To Stop Alarm	1=Fail To Stop Alarm must be acknowledged	Fail To Stop Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	Interlock Tripped Alarm Condition	Interlock Tripped Alarm Tag	1=Interlock Tripped Alarm exists and will be checked	1=Reset required to clear Interlock Trip Alarm	1=Interlock Tripped Alarm must be acknowledged	Interlock Trip Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	I/O Fault Alarm Condition	I/O Fault Alarm Tag	1=I/O Fault Alarm exists and will be checked	1=Reset required to clear I/O Fault Alarm	1=I/O Fault Alarm must be acknowledged	I/O Fault Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	1=OCmd_Stop any time, 0=OCmd_Stop only when Oper selected	1=XCmd_Stop any time, 0=XCmd_Stop only when Ext selected	1=New motor OCmd resets shed latches and cleared alarms, 0=OCmdReset reqd	1=New motor XCmd resets shed latches and cleared alarms, 0=OCmdReset reqd	1=Override ignores Bypassable Perm/ Intlk; 0=always use Perm/Intlk	1=Operator (unlocked) exists, can be selected	1=Operator Locked exists, can be selected	1=Program (unlocked) exists, can be selected	1=Program Locked exists, can be selected	1=External exists, can be selected	1=Maintenance exists, can be selected	1=Maintenance Out of Service exists, can be selected	1=Override supersedes Prog/Oper Lock, 0=don't override Lock	1=External supersedes Prog/Oper Lock, 0=don't override Lock	1=Power Up to Prog, 0=Power Up to Oper	Normal Source: 1=Program if no requests; 0=Operator if no requests	Command Priority: 1=Program Cmds Win; 0=Operator Cmds Win	1=PCmd_Prog used as a Level (1=Prog, 0=Oper)	1=PCmd_Lock used as a Level (1=Lock, 0=Unlock)	1=XCmd_Acq used as Level (1=Acq, 0=Rel)
		Usage:		Local	Local	Local	Local	Local	Local	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Local	Local	Local	Local	Local	Local	Local	Local	Input	Input	Input	Input	Input	Local	Local	Local	Local	Local	Local	Local	Local
		Data Type:		STRING_40	STRING_20	STRING_20	STRING_Area	STRING_16	STRING_16	REAL	BOOL	BOOL	BOOL	REAL	REAL	BOOL	BOOL	REAL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	REAL	REAL	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL
			(Origin)	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.FailToStart.Cfg_	.FailToStart.Cfg_	.FailToStart.Cfg_	.FailToStart.Cfg_	.FailToStart.Cfg_	.FailToStart.Cfg_	.FailToStart.Cfg_	.FailToStart.Cfg_	.FailToStop.Cfg_	.FailToStop.Cfg_	.FailToStop.Cfg_	.FailToStop.Cfg_	.FailToStop.Cfg_	.FailToStop.Cfg_	.FailToStop.Cfg_	.FailToStop.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_
Unit	Tag Description	TagName	Instance	Desc	Label	Tag	Area	FastText	SlowText	ChangeSpdT	AllowLocal	HasRunFdbk	UseRunFdbk	FailToStartT	FailToStopT	ShedOnFailToStart	ShedOnIOFault	SimFdbkT	HasSlowPermObj	HasFastPermObj	HasIntlkObj	HasResInhObj	HasRunTimeObj	HasOvldObj	HasMoreObj	HasJog	MaxJogT	StartHornT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	OperStopPrio	ExtStopPrio	OCmdResets	XCmdResets	OvrdPermIntlk	HasOper	HasOperLocked	HasProg	HasProgLocked	HasExt	HasMaint	HasMOoS	OvrdOverLock	ExtOverLock	ProgPwrUp	ProgNormal	PCmdPriority	PCmdProgAsLevel	PCmdLockAsLevel	ExtAcqAsLevel
		Default Values:	0	Two Speed Motor	Motor Control	P_Motor2Spd2Spd	area01	Fast	Low	3	0	0	0	10	10	1	1	2	0	0	0	0	0	0	0	0	0	0	Failed to Start	P_Motor2Spd.FailToStart	0	0	1	1000	0	1	5	480	Failed to Stop	P_Motor2Spd.FailToStop	0	0	1	1000	0	1	5	480	Interlock Trip	P_Motor2Spd.IntlkTrip	0	0	1	500	0	1	5	480	I/O Fault	P_Motor2Spd.IOFault	0	0	1	1000	0	1	5	480	0	0	0	0	0	1	1	1	1	0	1	1	1	0	0	0	0	0	0	0
		MyP_Motor2Spd	1	Reactor #7 Ventilation Fan	Reactor 7 Vent Fan	MyMotor2Spd	area01	Fast	Slow	20	1	1	1	5	5	1	1	2	0	0	1	0	0	1	0	0	0	0	Failed to Start	P_Motor2Spd.FailToSt	1	0	1	3	1	1	5	480	Failed to Stop	P_Motor2Spd.FailToSt	1	0	1	3	1	1	5	480	Interlock Trip	P_Motor2Spd.IntlkTri	1	0	1	3	1	1	5	480	I/O Fault	P_Motor2Spd.IOFault	1	0	1	3	1	1	5	480	1	0	0	0	0	1	1	1	1	0	1	1	1	0	0	0	0	0	0	0
			2
			3
			4
			5
			6
			7
			8
			9
			10
			11
			12
			13
			14
			15
			16
			17
			18
			19
			20
			21
			22
			23
			24
			25
			26
			27
			28
			29
			30	Strings too long to fit are formatted like this.
			31
			32
			33
			34
			35
			36
			37
			38
			39
			40
			41
			42
			43
			44
			45
			46
			47
			48
			49
			50
			51
			52
			53
			54
			55
			56
			57
			58
			59
			60
			61
			62
			63
			64
			65
			66
			67
			68
			69
			70
			71
			72
			73
			74
			75
			76
			77
			78
			79
			80
			81
			82
			83
			84
			85
			86
			87
			88
			89
			90
			91
			92
			93
			94
			95
			96
			97
			98
			99

## P_MotorHO
	P_MotorHO: Hand Operated Motor	Read From CLX:
		Send To CLX:

		Description:		Description for display on HMI	Label for graphic symbol displayed on HMI	Tagname for display on HMI	Process Area for security	Text for Running, Fast or Forward for display on HMI	Text for Slow or Reverse for display on HMI	1=Motor is 2 speed (fast, slow or stopped)	1=Motor is reversing (forward, reverse or stopped)	1=Trip Output is connected to motor, 0=Monitor only	After tripped, time to reach trip position before Alarm (sec)	1=Continue Trip and Alarm on Fail to Trip; 0=Alarm only on Fail to Trip	1=Trip Motor and Alarm on I/O Fault; 0=Alarm only on I/O Fault	Delay to echo back of Open/Closed status when in Simulation (sec)	1=Enable navigation to an Interlock object	1=Enable navigation to a Run Time object	1=Enable navigation to an Overload object (E3+, etc.)	1=Tells HMI an object with more info is available	Fail to Trip Alarm Condition	Fail to Trip Alarm Tag	1=Fail to Trip exists and will be checked	1=Reset required to clear Fail to Trip Alarm	1=Acknowledged required for Fail to Trip Alarm	Fail to Trip Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	Interlock Tripped Alarm Condition	Interlock Tripped Alarm Tag	1=Interlock Tripped Alarm exists and will be checked	1=Reset required to clear Interlock Trip Alarm	1=Acknowledge required for Interlock Trip Alarm	Interlock Trip Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	I/O Fault Alarm Condition	I/O Fault Alarm Tag	1=I/O Fault Alarm exists and will be checked	1=Reset required to clear I/O Fault Alarm	1=Acknowledge required for I/O Fault Alarm	I/O Fault Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	1=OCmd_Trip. Resets fault, 0=reset reqd to reset fault
		Usage:		Local	Local	Local	Local	Local	Local	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Local	Local	Local	Local	Local	Local	Local	Local	Input
		Data Type:		STRING_40	STRING_20	STRING_20	STRING_Area	STRING_16	STRING_16	BOOL	BOOL	BOOL	REAL	BOOL	BOOL	REAL	BOOL	BOOL	BOOL	BOOL	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	BOOL
			(Origin)	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.TripFail.Cfg_	.TripFail.Cfg_	.TripFail.Cfg_	.TripFail.Cfg_	.TripFail.Cfg_	.TripFail.Cfg_	.TripFail.Cfg_	.TripFail.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.Cfg_
Unit	Tag Description	TagName	Instance	Desc	Label	Tag	Area	FastFwdText	SlowRevText	2Spd	Rev	HasTrip	TripFailT	ShedOnFailToTrip	ShedOnIOFault	SimFdbkT	HasIntlkObj	HasRunTimeObj	HasOvldObj	HasMoreObj	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	OCmdResets
		Default Values:	0	Hand Operated Motor	Motor Monitor	P_MotorHO	area01	Running	Slow	0	0	0	10	1	1	3	0	0	0	0	Failed to Trip	P_MotorHO.FailToTrip	0	0	1	1000	0	1	5	480	Interlock Trip	P_MotorHO.IntlkTrip	0	0	1	500	0	1	5	480	I/O Fault	P_MotorHO.IOFault	0	0	1	1000	0	1	5	480	0
		MyP_MotorHO	1	Hand Operated Motor	Motor Monitor	P_MotorHO	area01	Running	Slow	0	0	0	10	1	1	3	0	0	0	0	Failed to Trip	XAS-nnnnA	0	0	1	3	1	1	5	0	Interlock Trip	XAS-nnnnB	0	0	1	500	1	1	5	0	I/O Fault	XAF-nnnn	1	0	1	1000	1	1	5	480	0
			2
			3
			4
			5
			6
			7
			8
			9
			10
			11
			12
			13
			14
			15
			16
			17
			18
			20
			21
			22
			23
			24
			25
			26
			27
			28
			29
			30	Strings too long to fit are formatted like this.
			31
			32
			33
			34
			35
			36
			37
			38
			39
			40
			41
			42
			43
			44
			45
			46
			47
			48
			49
			50
			51
			52
			53
			54
			55
			56
			57
			58
			59
			60
			61
			62
			63
			64
			65
			66
			67
			68
			69
			70
			71
			72
			73
			74
			75
			76
			77
			78
			79
			80
			81
			82
			83
			84
			85
			86
			87
			88
			89
			90
			91
			92
			93
			94
			95
			96
			97
			98
			99

## P_MotorRev
	P_MotorRev: Reversing Motor	Read From CLX:
		Send To CLX:

		Description:		Description for display on HMI	Label for graphic symbol displayed on HMI	Tagname for display on HMI	Process Area for security	Description for Forward direction	Description for Reverse direction	Delay with contactors open when changing directions (sec)	1=Allow Local Start/Stop without alarm, 0=Start/Stop from HMI/prog only	1=Motor provides run feedback signals	1=Use motor run feedback siignals for failure checking	Time after Start to get correct Run Feedback before Fault (sec)	Time after Stop to drop Run Feedbacks before Fault (sec)	1=Stop Motor and Alarm on Fail to Start; 0=Alarm only on Fail to Start	1=Stop Motor and Alarm on I/O Fault; 0=Alarm only on I/O Fault	Delay to echo back of Running/Stopped status when in Simulation (sec)	1=Tells HMI a P_Perm is connected to Inp_FwdPerm	1=Tells HMI a P_Perm is connected to Inp_RevPerm	1=Tells HMI a P_Intlk is connected to Inp_Intlk	1=Tell HMI a P_ResInh Restart Inhibit is connected	1=Tells HMI a P_RunTime is connected	1=Tell HMI an Overload object exists (E3+,etc.)	1=Tells HMI an object with more info is available	1=Motor Jog Command enabled/visible, 0=Motor Jog Command not allowed	Maximum jog time (sec, 0=unlimited)	Time to sound audible on commanded start (sec) (0=disabled)	Fail To Start Alarm Condition	Fail To Start Alarm Tag	1=Fail To Start Alarm exists and will be checked	1=Reset required to clear Fail To Start Alarm	1=Fail To Start Alarm must be acknowledged	Fail To Start Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	Fail To Stop Alarm Condition	Fail To Stop Alarm Tag	1=Fail To Stop Alarm exists and will be checked	1=Reset required to clear Fail To Stop Alarm	1=Fail To Stop Alarm must be acknowledged	Fail To Stop Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	Interlock Tripped Alarm Condition	Interlock Tripped Alarm Tag	1=Interlock Tripped Alarm exists and will be checked	1=Reset required to clear Interlock Trip Alarm	1=Acknowledge required for Interlock Trip Alarm	Interlock Trip Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	I/O Fault Alarm Condition	I/O Fault Alarm Tag	1=I/O Fault Alarm exists and will be checked	1=Reset required to clear I/O Fault Alarm	1=Acknowledge required for I/O Fault Alarm	I/O Fault Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	1=OCmd_Stop any time, 0=OCmd_Stop only when Oper selected	1=XCmd_Stop any time, 0=XCmd_Stop only when Ext selected	1=New motor OCmd resets shed latches and cleared alarms, 0=OCmdReset reqd	1=New motor XCmd resets shed latches and cleared alarms, 0=OCmdReset reqd	1=Override ignores Bypassable Perm/ Intlk; 0=always use Perm/Intlk	1=Operator (unlocked) exists, can be selected	1=Operator Locked exists, can be selected	1=Program (unlocked) exists, can be selected	1=Program Locked exists, can be selected	1=External exists, can be selected	1=Maintenance exists, can be selected	1=Maintenance Out of Service exists, can be selected	1=Override supersedes Prog/Oper Lock, 0=don't override Lock	1=External supersedes Prog/Oper Lock, 0=don't override Lock	1=Power Up to Prog, 0=Power Up to Oper	Normal Source: 1=Program if no requests; 0=Operator if no requests	Command Priority: 1=Program Cmds Win; 0=Operator Cmds Win	1=PCmd_Prog used as a Level (1=Prog, 0=Oper)	1=PCmd_Lock used as a Level (1=Lock, 0=Unlock)	1=XCmd_Acq used as Level (1=Acq, 0=Rel)
		Usage:		Local	Local	Local	Local	Local	Local	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Local	Local	Local	Local	Local	Local	Local	Local	Input	Input	Input	Input	Input	Local	Local	Local	Local	Local	Local	Local	Local
		Data Type:		STRING_40	STRING_20	STRING_20	STRING_Area	STRING_16	STRING_16	REAL	BOOL	BOOL	BOOL	REAL	REAL	BOOL	BOOL	REAL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	REAL	REAL	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL
			(Origin)	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.FailToStart.Cfg_	.FailToStart.Cfg_	.FailToStart.Cfg_	.FailToStart.Cfg_	.FailToStart.Cfg_	.FailToStart.Cfg_	.FailToStart.Cfg_	.FailToStart.Cfg_	.FailToStop.Cfg_	.FailToStop.Cfg_	.FailToStop.Cfg_	.FailToStop.Cfg_	.FailToStop.Cfg_	.FailToStop.Cfg_	.FailToStop.Cfg_	.FailToStop.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_
Unit	Tag Description	TagName	Instance	Desc	Label	Tag	Area	FwdText	RevText	ChangeDirT	AllowLocal	HasRunFdbk	UseRunFdbk	FailToStartT	FailToStopT	ShedOnFailToStart	ShedOnIOFault	SimFdbkT	HasFwdPermObj	HasRevPermObj	HasIntlkObj	HasResInhObj	HasRunTimeObj	HasOvldObj	HasMoreObj	HasJog	MaxJogT	StartHornT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	OperStopPrio	ExtStopPrio	OCmdResets	XCmdResets	OvrdPermIntlk	HasOper	HasOperLocked	HasProg	HasProgLocked	HasExt	HasMaint	HasMOoS	OvrdOverLock	ExtOverLock	ProgPwrUp	ProgNormal	PCmdPriority	PCmdProgAsLevel	PCmdLockAsLevel	ExtAcqAsLevel
		Default Values:	0	Reversing Motor	Motor Control	P_MotorRev	area01	Forward	Reverse	3	0	0	0	10	10	1	1	2	0	0	0	0	0	0	0	0	0	0	Failed to Start	P_MotorRev.FailToSt	0	0	1	1000	0	1	5	480	Failed to Stop	P_MotorRev.FailToSt	0	0	1	1000	0	1	5	480	Interlock Trip	P_MotorRev.IntlkTrip	0	0	1	500	0	1	5	480	I/O Fault	P_MotorRev.IOFault	1	0	1	1000	0	1	5	480	0	0	0	0	0	1	1	1	1	0	1	1	1	0	0	0	0	0	0	0
		MyP_MotorRev	1	Fresh Leaf Transfer Conveyor	Fresh Leaf	M623	area01	Forward	Reverse	20	0	0	0	5	5	1	1	2	0	0	1	0	0	1	0	0	0	0	Failed to Start	P_MotorRev.FailToSt	0	0	1	3	1	1	5	480	Failed to Stop	P_MotorRev.FailToSt	0	0	1	3	1	1	5	480	Interlock Trip	P_MotorRev.IntlkTrip	1	0	1	3	1	1	5	480	I/O Fault	P_MotorRev.IOFault	1	0	1	3	1	1	5	480	0	0	0	0	0	1	1	1	1	0	1	1	1	0	0	0	0	0	0	0
			2
			3
			4
			5
			6
			7
			8
			9
			10
			11
			12
			13
			14
			15
			16
			17
			18
			19
			20
			21
			22
			23
			24
			25
			26
			27
			28
			29
			30	Strings too long to fit are formatted like this.
			31
			32
			33
			34
			35
			36
			37
			38
			39
			40
			41
			42
			43
			44
			45
			46
			47
			48
			49
			50
			51
			52
			53
			54
			55
			56
			57
			58
			59
			60
			61
			62
			63
			64
			65
			66
			67
			68
			69
			70
			71
			72
			73
			74
			75
			76
			77
			78
			79
			80
			81
			82
			83
			84
			85
			86
			87
			88
			89
			90
			91
			92
			93
			94
			95
			96
			97
			98
			99

## P_nPos
	P_nPos: n-Position (up to 8) Device	Read From CLX:
		Send To CLX:

		Description:		Description for display on HMI	Label for graphic symbol displayed on HMI	Tagname for display on HMI	Process Area for security	Number of Device Positions (2 .. 8)	Description for Position 1 on HMI	Description for Position 2 on HMI	Description for Position 3 on HMI	Description for Position 4 on HMI	Description for Position 5 on HMI	Description for Position 6 on HMI	Description for Position 7 on HMI	Description for Position 8 on HMI	1=Positions are circular (rotary device, after Pos n is Pos 1)	1=Circular (rotary) device can only rotate "clockwise", 0=bidirectional (use shortest path)	1=Drive Linear device to Pos 1 on every move; 0=move direct to cmd pos	Number of Retries via Pos 1 before declaring failure (0=dont retry)	Delay before extending cylinder to engage for move (sec)	Delay to verify device has settled in commanded position (sec)	1=Drive to Pos 1 on Interlock or Fault; 0=De-energize only	1=Latch in Out_PosX until new Position commanded	1=New pos. cmd. OK during move, 0=must wait for prev. cmd. to finish	1=Must sequence a position lock or seal	1=Device has feedback for all positions	1=Position Feedback shall be used to check device position	Max time to reach target position before fail (sec)	1=Device has locked / unlocked feedback	1=Lock Feedback shall be used to verify locking and unlocking	Max time to get locked / unlocked feedback before fail (sec)	1=Device indexing cylinders have position feedback	1=Indexing cylinder position feedback shall be checked	1=De-energize Device and Alarm on Position Fail; 0=Alarm only	1=De-energize Device and Alarm on Lock Fail; 0=Alarm only	1=De-energize Device and Alarm on I/O Fault; 0=Alarm only	Time to reach target position in simulation (sec)	Time to lock or unlock in simulation (sec)	Time to simulate index cylinder feedback in simulation (sec)	0 = Horn on energize only, 1 = Horn on any state change	Time to sound audible on commanded energize (sec) (0=disabled)	1=Tells HMI a P_Perm is connected to Inp_Perm	1=Tells HMI a P_Intlk is connected to Inp_Intlk	1=Tells HMI an object with more info is available	Position Failure Alarm Condition	Position Failure Alarm Tag	1=Position Failure Alarm exists and will be checked	1=Position Failure Alarm is latched in, requires Reset Command to clear	1=Position Failure Alarm must be acknowledged	Position Failure Alarm Severity: 1=info, 2=warn, 3=excep, 4=fault	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	Lock/Unlock Failure Alarm Condition	Lock/Unlock Failure Alarm Tag	1=Lock/Unlock Failure Alarm exists and will be checked	1=Lock/Unlock Failure Alarm is latched in, requires Reset Command to clear	1=Lock/Unlock Failure Alarm must be acknowledged	Lock/Unlock Failure Alarm Severity: 1=info, 2=warn, 3=excep, 4=fault	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	Interlock Tripped Alarm Condition	Interlock Tripped Alarm Tag	1=Interlock Tripped Alarm exists and will be checked	1=Interlock Tripped Alarm is latched in, requires Reset Command to clear	1=Interlock Tripped Alarm must be acknowledged	Interlock Tripped Alarm Severity: 1=info, 2=warn, 3=excep, 4=fault	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	I/O Fault Alarm Condition	I/O Fault Alarm Tag	1=I/O Fault Alarm exists and will be checked	1=I/O Fault Alarm is latched in, requires Reset Command to clear	1=I/O Fault Alarm must be acknowledged	I/O Fault Alarm Severity: 1=info, 2=warn, 3=excep, 4=fault	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	1=New device OCmd resets shed latches and cleared alarms, 0=OCmdReset reqd	1=New device XCmd resets shed latches and cleared alarms, 0=XCmdReset reqd	1=Override ignores Bypassable Perm/ Intlk; 0=always use Perm/Intlk	1=Operator (unlocked) exists, can be selected	1=Operator Locked exists, can be selected	1=Program (unlocked) exists, can be selected	1=Program Locked exists, can be selected	1=External exists, can be selected	1=Maintenance exists, can be selected	1=Maintenance Out of Service exists, can be selected	1=Override supersedes Prog/Oper Lock, 0=don't override Lock	1=External supersedes Prog/Oper Lock, 0=don't override Lock	1=Power Up to Prog, 0=Power Up to Oper	Normal Source: 1=Program if no requests; 0=Operator if no requests	Command Priority: 1=Program Cmds Win; 0=Operator Cmds Win	1=PCmd_Prog used as a Level (1=Prog, 0=Oper)	1=PCmd_Lock used as a Level (1=Lock, 0=Unlock)	1=XCmd_Acq used as Level (1=Acq, 0=Rel)
		Usage:		Local	Local	Local	Local	Input	Local	Local	Local	Local	Local	Local	Local	Local	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Local	Local	Local	Local	Local	Local	Local	Local	Input	Input	Input	Local	Local	Local	Local	Local	Local	Local	Local
		Data Type:		STRING_40	STRING_20	STRING_20	STRING_Area	DINT	STRING_16	STRING_16	STRING_16	STRING_16	STRING_16	STRING_16	STRING_16	STRING_16	BOOL	BOOL	BOOL	DINT	REAL	REAL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	REAL	BOOL	BOOL	REAL	BOOL	BOOL	BOOL	BOOL	BOOL	REAL	REAL	REAL	BOOL	REAL	BOOL	BOOL	BOOL	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL
			(Origin)	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.PosFail.Cfg_	.PosFail.Cfg_	.PosFail.Cfg_	.PosFail.Cfg_	.PosFail.Cfg_	.PosFail.Cfg_	.PosFail.Cfg_	.PosFail.Cfg_	.LockFail.Cfg_	.LockFail.Cfg_	.LockFail.Cfg_	.LockFail.Cfg_	.LockFail.Cfg_	.LockFail.Cfg_	.LockFail.Cfg_	.LockFail.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.Cfg_	.Cfg_	.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_
Unit	Tag Description	TagName	Instance	Desc	Label	Tag	Area	NumPos	Pos1Name	Pos2Name	Pos3Name	Pos4Name	Pos5Name	Pos6Name	Pos7Name	Pos8Name	Circ	CWOnly	ViaPos1	Retries	ExtendT	VerifyT	IntlkToPos1	OutPosLatch	CmdDuringMove	HasLock	HasPosFdbk	UsePosFdbk	PosChkT	HasLockFdbk	UseLockFdbk	LockChkT	HasCylFdbk	UseCylFdbk	ShedOnPosFail	ShedOnLockFail	ShedOnIOFault	PosSimT	LockSimT	CylSimT	HornOnChange	StartHornT	HasPermObj	HasIntlkObj	HasMoreObj	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	OCmdResets	XCmdResets	OvrdPermIntlk	HasOper	HasOperLocked	HasProg	HasProgLocked	HasExt	HasMaint	HasMOoS	OvrdOverLock	ExtOverLock	ProgPwrUp	ProgNormal	PCmdPriority	PCmdProgAsLevel	PCmdLockAsLevel	ExtAcqAsLevel
		Default Values:	0	n-Position Device	n-Position Device	P_nPos	area01	3	Position 1	Position 2	Position 3	Position 4	Position 5	Position 6	Position 7	Position 8	0	0	0	0	0.0	1.0	0	0	0	0	0	0	30	0	0	5	0	0	1	1	1	1.0	1.0	1.0	1	0	0	0	0	Position Failure	P_nPos.PosFail	1	0	1	1000	0	1	5	480	Lock/Unlock Failure	P_nPos.LockFail	1	0	1	1000	0	1	5	480	Interlock Trip	P_nPos.IntlkTrip	1	0	1	500	0	1	5	480	I/O Fault	P_nPos.IOFault	1	0	1	1000	0	1	5	480	0	0	0	1	1	1	1	0	1	1	1	0	0	0	0	0	0	0
		MyP_nPos	1	n-Position Device	n-Position Device	My_P_nPos	area01	8	Everywhere	Somewhere	Anywhere	Elsewhere	Nowhere	Softwhere	Hardwhere	Underwhere	1	0	0	0	0	1	0	0	1	1	1	1	60	0	0	5	1	1	0	0	0	1	1	1	0	0	1	1	0	Position Failure	My_P_nPos.PosFail	1	0	1	3	1	1	5	480	Lock/Unlock Failure	My_P_nPos.LockFail	0	0	1	3	1	1	5	480	Interlock Trip	My_P_nPos.IntlkTrip	1	0	1	3	1	1	5	480	I/O Fault	My_P_nPos.IOFault	1	0	1	3	1	1	5	480	1	0	0	1	1	1	1	0	1	1	1	0	0	0	0	0	0	0
			2
			3
			4
			5
			6
			7
			8
			9
			10
			11
			12
			13
			14
			15
			16
			17
			18
			19
			20
			21
			22
			23
			24
			25
			26
			27
			28
			29
			30	Strings too long to fit are formatted like this.
			31
			32
			33
			34
			35
			36
			37
			38
			39
			40
			41
			42
			43
			44
			45
			46
			47
			48
			49
			50
			51
			52
			53
			54
			55
			56
			57
			58
			59
			60
			61
			62
			63
			64
			65
			66
			67
			68
			69
			70
			71
			72
			73
			74
			75
			76
			77
			78
			79
			80
			81
			82
			83
			84
			85
			86
			87
			88
			89
			90
			91
			92
			93
			94
			95
			96
			97
			98
			99

## P_Perm
	P_Perm: Permissives	Read From CLX:
		Send To CLX:

		Description:		Description for display on HMI	Label for graphic symbol displayed on HMI	Tagname for display on HMI	Process Area for security	1=Tells HMI an object with more info is available	Short HMI description of Permissive Condition 0	Bit indicates which state (0 or 1) of Inp_Perm00 is OK to run	1=Permissive 00 can be bypassed	Tagname for destinations of Navigation button 0	1=Enable Navigation Button 0	Short HMI description of Permissive Condition 1	Bit indicates which state (0 or 1) of Inp_Perm01 is OK to run	1=Permissive 01 can be bypassed	Tagname for destinations of Navigation button 1	1=Enable Navigation Button 1	Short HMI description of Permissive Condition 2	Bit indicates which state (0 or 1) of Inp_Perm02 is OK to run	1=Permissive 02 can be bypassed	Tagname for destinations of Navigation button 2	1=Enable Navigation Button 2	Short HMI description of Permissive Condition 3	Bit indicates which state (0 or 1) of Inp_Perm03 is OK to run	1=Permissive 03 can be bypassed	Tagname for destinations of Navigation button 3	1=Enable Navigation Button 3	Short HMI description of Permissive Condition 4	Bit indicates which state (0 or 1) of Inp_Perm04 is OK to run	1=Permissive 04 can be bypassed	Tagname for destinations of Navigation button 4	1=Enable Navigation Button 4	Short HMI description of Permissive Condition 5	Bit indicates which state (0 or 1) of Inp_Perm05 is OK to run	1=Permissive 05 can be bypassed	Tagname for destinations of Navigation button 5	1=Enable Navigation Button 5	Short HMI description of Permissive Condition 6	Bit indicates which state (0 or 1) of Inp_Perm06 is OK to run	1=Permissive 06 can be bypassed	Tagname for destinations of Navigation button 6	1=Enable Navigation Button 6	Short HMI description of Permissive Condition 7	Bit indicates which state (0 or 1) of Inp_Perm07 is OK to run	1=Permissive 07 can be bypassed	Tagname for destinations of Navigation button 7	1=Enable Navigation Button 7	Short HMI description of Permissive Condition 8	Bit indicates which state (0 or 1) of Inp_Perm08 is OK to run	1=Permissive 08 can be bypassed	Tagname for destinations of Navigation button 8	1=Enable Navigation Button 8	Short HMI description of Permissive Condition 9	Bit indicates which state (0 or 1) of Inp_Perm09 is OK to run	1=Permissive 09 can be bypassed	Tagname for destinations of Navigation button 9	1=Enable Navigation Button 9	Short HMI description of Permissive Condition 10	Bit indicates which state (0 or 1) of Inp_Perm10 is OK to run	1=Permissive 10 can be bypassed	Tagname for destinations of Navigation button 10	1=Enable Navigation Button 10	Short HMI description of Permissive Condition 11	Bit indicates which state (0 or 1) of Inp_Perm11 is OK to run	1=Permissive 11 can be bypassed	Tagname for destinations of Navigation button 11	1=Enable Navigation Button 11	Short HMI description of Permissive Condition 12	Bit indicates which state (0 or 1) of Inp_Perm12 is OK to run	1=Permissive 12 can be bypassed	Tagname for destinations of Navigation button 12	1=Enable Navigation Button 12	Short HMI description of Permissive Condition 13	Bit indicates which state (0 or 1) of Inp_Perm13 is OK to run	1=Permissive 13 can be bypassed	Tagname for destinations of Navigation button 13	1=Enable Navigation Button 13	Short HMI description of Permissive Condition 14	Bit indicates which state (0 or 1) of Inp_Perm14 is OK to run	1=Permissive 14 can be bypassed	Tagname for destinations of Navigation button 14	1=Enable Navigation Button 14	Short HMI description of Permissive Condition 15	Bit indicates which state (0 or 1) of Inp_Perm15 is OK to run	1=Permissive 15 can be bypassed	Tagname for destinations of Navigation button 15	1=Enable Navigation Button 15
		Usage:		Local	Local	Local	Local	Input	Local	Input	Input	Local	Input	Local	Input	Input	Local	Input	Local	Input	Input	Local	Input	Local	Input	Input	Local	Input	Local	Input	Input	Local	Input	Local	Input	Input	Local	Input	Local	Input	Input	Local	Input	Local	Input	Input	Local	Input	Local	Input	Input	Local	Input	Local	Input	Input	Local	Input	Local	Input	Input	Local	Input	Local	Input	Input	Local	Input	Local	Input	Input	Local	Input	Local	Input	Input	Local	Input	Local	Input	Input	Local	Input	Local	Input	Input	Local	Input
		Data Type:		STRING_40	STRING_20	STRING_20	STRING_Area	BOOL	STRING_Cond	BOOL	BOOL	STRING_NavTag	BOOL	STRING_Cond	BOOL	BOOL	STRING_NavTag	BOOL	STRING_Cond	BOOL	BOOL	STRING_NavTag	BOOL	STRING_Cond	BOOL	BOOL	STRING_NavTag	BOOL	STRING_Cond	BOOL	BOOL	STRING_NavTag	BOOL	STRING_Cond	BOOL	BOOL	STRING_NavTag	BOOL	STRING_Cond	BOOL	BOOL	STRING_NavTag	BOOL	STRING_Cond	BOOL	BOOL	STRING_NavTag	BOOL	STRING_Cond	BOOL	BOOL	STRING_NavTag	BOOL	STRING_Cond	BOOL	BOOL	STRING_NavTag	BOOL	STRING_Cond	BOOL	BOOL	STRING_NavTag	BOOL	STRING_Cond	BOOL	BOOL	STRING_NavTag	BOOL	STRING_Cond	BOOL	BOOL	STRING_NavTag	BOOL	STRING_Cond	BOOL	BOOL	STRING_NavTag	BOOL	STRING_Cond	BOOL	BOOL	STRING_NavTag	BOOL	STRING_Cond	BOOL	BOOL	STRING_NavTag	BOOL
			(Origin)	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_
Unit	Tag Description	TagName	Instance	Desc	Label	Tag	Area	HasMoreObj	CondTxt[0]	OKState.0	Bypassable.0	NavTag[0]	HasNav.0	CondTxt[1]	OKState.1	Bypassable.1	NavTag[1]	HasNav.1	CondTxt[2]	OKState.2	Bypassable.2	NavTag[2]	HasNav.2	CondTxt[3]	OKState.3	Bypassable.3	NavTag[3]	HasNav.3	CondTxt[4]	OKState.4	Bypassable.4	NavTag[4]	HasNav.4	CondTxt[5]	OKState.5	Bypassable.5	NavTag[5]	HasNav.5	CondTxt[6]	OKState.6	Bypassable.6	NavTag[6]	HasNav.6	CondTxt[7]	OKState.7	Bypassable.7	NavTag[7]	HasNav.7	CondTxt[8]	OKState.8	Bypassable.8	NavTag[8]	HasNav.8	CondTxt[9]	OKState.9	Bypassable.9	NavTag[9]	HasNav.9	CondTxt[10]	OKState.10	Bypassable.10	NavTag[10]	HasNav.10	CondTxt[11]	OKState.11	Bypassable.11	NavTag[11]	HasNav.11	CondTxt[12]	OKState.12	Bypassable.12	NavTag[12]	HasNav.12	CondTxt[13]	OKState.13	Bypassable.13	NavTag[13]	HasNav.13	CondTxt[14]	OKState.14	Bypassable.14	NavTag[14]	HasNav.14	CondTxt[15]	OKState.15	Bypassable.15	NavTag[15]	HasNav.15
		Default Values:	0	Permissives	Permissives	P_Perm	area01	0	Enter Description #0	1	0		0		1	0		0		1	0		0		1	0		0		1	0		0		1	0		0		1	0		0		1	0		0		1	0		0		1	0		0		1	0		0		1	0		0		1	0		0		1	0		0		1	0		0		1	0		0
		P1_Motor_Perm	1	Permissives	Permissives	P_Perm	area01	0	Group Permissive	1	1		0	Group Non-Byp. Perm	1	0		0	Restart Inhibited	1	1		0		1	0		0		1	0		0		1	0		0		1	0		0		1	0		0		1	0		0		1	0		0		1	0		0		1	0		0		1	0		0		1	0		0		1	0		0		1	0		0
			2
			3
			4
			5
			6
			7
			8
			9
			10
			11
			12
			13
			14
			15
			16
			17
			18
			19
			20
			21
			22
			23
			24
			25
			26
			27
			28
			29
			30	Strings too long to fit are formatted like this.
			31
			32
			33
			34
			35
			36
			37
			38
			39
			40
			41
			42
			43
			44
			45
			46
			47
			48
			49
			50
			51
			52
			53
			54
			55
			56
			57
			58
			59
			60
			61
			62
			63
			64
			65
			66
			67
			68
			69
			70
			71
			72
			73
			74
			75
			76
			77
			78
			79
			80
			81
			82
			83
			84
			85
			86
			87
			88
			89
			90
			91
			92
			93
			94
			95
			96
			97
			98
			99

## P_PF52x
	P_PF52x: PowerFlex 523 / 525 Variable Frequency Drive	Read From CLX:
		Send To CLX:

		Description:		Description for display on HMI	Label for graphic symbol displayed on HMI	Tagname for display on HMI	Process Area for security	Drive Digital Input 1 Label	Drive Digital Input 2 Label	Drive Digital Input 3 Label	Drive Digital Input 4 Label	Drive Digital Input 4 Label	Drive Digital Input 4 Label	Drive Digital Input 4 Label	Drive Digital Input 4 Label	1=Drive can be run reverse, 0=Forward only	1=Drive Jog Command enabled/visible, 0=Drive Jog Command not allowed	1=Allow Local Start/Stop without alarm, 0=Start/Stop from HMI/prog only	1=Tells HMI a P_Perm is connected to Inp_FwdPerm	1=Tells HMI a P_Perm is connected to Inp_RevPerm	1=Tells HMI a P_Intlk is connected to Inp_Intlk	1=Tells HMI a P_ResInh Restart Inhibit is connected	1=Tells HMI a P_RunTime is connected	1=Tells HMI an object with more info is available	1=PSets track OSets in Oper, OSets track PSets in Prog, 0=no tracking	1=Prog/Oper Settings track Override/Hand speed reference	1=OCmd_Stop any time, 0=OCmd_Stop only when Oper selected	1=XCmd_Stop any time, 0=XCmd_Stop only when Ext selected	1=New drive OCmd resets shed latches and cleared alarms, 0=OCmdReset reqd	1=New Device XCmd resets shed latches and cleared alarms, 0=XCmdReset reqd	1=Override ignores Bypassable Perm/ Intlk; 0=always use Perm/Intlk	1=Stop Motor and Alarm on Fail to Start; 0=Alarm only on Fail to Start	1=Stop Motor and Alarm on I/O Fault; 0=Alarm only on I/O Fault	1=In simulation, scale Speed Ref EU to Speed Fdbk EU	1=In simulation, scale Speed Ref EU to raw, then raw to Speed Fdbk EU	Minimum Speed Reference in EU (for limiting)	Maximum Speed Reference in EU (for limiting)	Speed Reference Minimum in Drive (raw) Units (for scaling)	Speed Reference Maximum in Drive (raw) Units (for scaling)	Speed Reference Minimum in Engineering Units (for scaling)	Speed Reference Maximum in Engineering Units (for scaling)	Number of decimal places for CV display (0..6)	Speed Feedback Minimum in Drive (raw) Units (for scaling)	Speed Feedback Maximum in Drive (raw) Units (for scaling)	Speed Feedback Maximum in Engineering Units (for scaling)	Speed Feedback Minimum in Engineering Units (for scaling)	Time to ramp speed fdbk when in Simulation (sec)	Time after Start to get Run Feedback before Fault (sec)	Time after Stop to drop Run Feedback before Fault (sec)	Time to pulse Out_Reset to clear drive fault	Maximum jog time (sec, 0=unlimited)	Time to sound audible on commanded start (sec) (0=disabled)	Oper keeps control in Prog Mode: .0=Reference, .1=Start/Stop, .2=Fwd/Rev	Prog keeps control in Oper Mode: .0=Reference, .1=Start/Stop, .2=Fwd/Rev	Prog keeps control in Oper Mode: .0=Reference, .1=Start/Stop, .2=Fwd/Rev	1=Acknowledge required for Drive Fault Alarm	Drive Faulted Alarm	Drive Faulted Alarm	Drive Faulted Alarm	Drive Faulted Alarm	1=Drive Fault Alarm exists and will be checked	Drive Faulted Alarm	1=Reset required to clear Drive Fault Alarm	Drive Fault Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	Drive Faulted Alarm	1=Fail To Start Alarm must be acknowledged	Drive Failed to Start Alarm	Drive Failed to Start Alarm	Drive Failed to Start Alarm	Drive Failed to Start Alarm	1=Fail To Start Alarm exists and will be checked	Drive Failed to Start Alarm	1=Reset required to clear Fail To Start Alarm	Fail To Start Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	Drive Failed to Start Alarm	1=Fail To Stop Alarm must be acknowledged	Drive Failed to Stop Alarm	Drive Failed to Stop Alarm	Drive Failed to Stop Alarm	Drive Failed to Stop Alarm	1=Fail To Stop Alarm exists and will be checked	Drive Failed to Stop Alarm	1=Reset required to clear Fail To Stop Alarm	Fail To Stop Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	Drive Failed to Stop Alarm	1=Acknowledge required for Interlock Trip Alarm	Interlock Trip Alarm	Interlock Trip Alarm	Interlock Trip Alarm	Interlock Trip Alarm	1=Interlock Tripped Alarm exists and will be checked	Interlock Trip Alarm	1=Reset required to clear Interlock Trip Alarm	Interlock Trip Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	Interlock Trip Alarm	1=Acknowledge required for I/O Fault Alarm	I/O Fault Alarm	I/O Fault Alarm	I/O Fault Alarm	I/O Fault Alarm	1=I/O Fault Alarm exists and will be checked	I/O Fault Alarm	1=Reset required to clear I/O Fault Alarm	I/O Fault Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	I/O Fault Alarm	1=Operator (unlocked) exists, can be selected	1=Operator Locked exists, can be selected	1=Program (unlocked) exists, can be selected	1=Program Locked exists, can be selected	1=External exists, can be selected	1=Maintenance exists, can be selected	1=Maintenance Out of Service exists, can be selected	1=Override supersedes Prog/Oper Lock, 0=don't override Lock	1=External supersedes Prog/Oper Lock, 0=don't override Lock	1=Power Up to Prog, 0=Power Up to Oper	Normal Source: 1=Program if no requests; 0=Operator if no requests	Command Priority: 1=Program Cmds Win; 0=Operator Cmds Win	1=PCmd_Prog used as a Level (1=Prog, 0=Oper)	1=PCmd_Lock used as a Level (1=Lock, 0=Unlock)	1=XCmd_Acq used as Level (1=Acq, 0=Rel)
		Usage:		Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local
		Data Type:		STRING_40	STRING_20	STRING_20	STRING_Area	STRING_20	STRING_20	STRING_20	STRING_20	STRING_16	STRING_16	STRING_8	STRING_8	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	REAL	REAL	DINT	DINT	REAL	REAL	DINT	DINT	DINT	REAL	REAL	REAL	REAL	REAL	REAL	REAL	REAL	SINT	SINT	SINT	BOOL	BOOL	BOOL	DINT	STRING_20	BOOL	DINT	BOOL	DINT	STRING_20	BOOL	BOOL	BOOL	DINT	STRING_20	BOOL	DINT	BOOL	DINT	STRING_20	BOOL	BOOL	BOOL	DINT	STRING_20	BOOL	DINT	BOOL	DINT	STRING_20	BOOL	BOOL	BOOL	DINT	STRING_20	BOOL	DINT	BOOL	DINT	STRING_20	BOOL	BOOL	BOOL	DINT	STRING_20	BOOL	DINT	BOOL	DINT	STRING_20	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL
			(Origin)	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.DriveFault.Cfg_	.DriveFault.Cfg_	.DriveFault.Cfg_	.DriveFault.Cfg_	.DriveFault.Cfg_	.DriveFault.Cfg_	.DriveFault.Cfg_	.DriveFault.Cfg_	.FailToStart.Cfg_	.FailToStart.Cfg_	.FailToStart.Cfg_	.FailToStart.Cfg_	.FailToStart.Cfg_	.FailToStart.Cfg_	.FailToStart.Cfg_	.FailToStart.Cfg_	.FailToStop.Cfg_	.FailToStop.Cfg_	.FailToStop.Cfg_	.FailToStop.Cfg_	.FailToStop.Cfg_	.FailToStop.Cfg_	.FailToStop.Cfg_	.FailToStop.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_
Unit	Tag Description	TagName	Instance	Desc	Label	Tag	Area	DigIn1Txt	DigIn2Txt	DigIn3Txt	DigIn4Txt	FwdText	RevText	SpeedRefEU	SpeedFdbkEU	HasReverse	HasJog	AllowLocal	HasFwdPermObj	HasRevPermObj	HasIntlkObj	HasResInhObj	HasRunTimeObj	HasMoreObj	SetTrack	SetTrackOvrdHand	OperStopPrio	ExtStopPrio	OCmdResets	XCmdResets	OvrdPermIntlk	ShedOnFailToStart	ShedOnIOFault	SimScaleEU	SimScaleRaw	MinSpdRef	MaxSpdRef	SpeedRefRawMin	SpeedRefRawMax	SpeedRefEUMin	SpeedRefEUMax	DecPlcs	SpeedFdbkRawMin	SpeedFdbkRawMax	SpeedFdbkEUMax	SpeedFdbkEUMin	SimRampT	FailToStartT	FailToStopT	ResetPulseT	MaxJogT	StartHornT	OperKeep	ProgKeep	ExtKeep	AckReqd	AllowDisable	AllowShelve	AlmMinOnT	Cond	Exists	MaxShelfT	ResetReqd	Severity	Tag	AckReqd	AllowDisable	AllowShelve	AlmMinOnT	Cond	Exists	MaxShelfT	ResetReqd	Severity	Tag	AckReqd	AllowDisable	AllowShelve	AlmMinOnT	Cond	Exists	MaxShelfT	ResetReqd	Severity	Tag	AckReqd	AllowDisable	AllowShelve	AlmMinOnT	Cond	Exists	MaxShelfT	ResetReqd	Severity	Tag	AckReqd	AllowDisable	AllowShelve	AlmMinOnT	Cond	Exists	MaxShelfT	ResetReqd	Severity	Tag	HasOper	HasOperLocked	HasProg	HasProgLocked	HasExt	HasMaint	HasMOoS	OvrdOverLock	ExtOverLock	ProgPwrUp	ProgNormal	PCmdPriority	PCmdProgAsLevel	PCmdLockAsLevel	ExtAcqAsLevel
		Default Values:	0	PF523 / PF525 Variable Frequency Drive	Motor Speed Control	P_PF52x	area01	Digital Input 1	Digital Input 2	Digital Input 3	Digital Input 4	Forward	Reverse	Hz	Hz	0	0	0	0	0	0	0	0	0	1	0	0	0	0	0	0	1	1	0	0	0	60	0	6000	0	60	2	0	6000	60	0	10	15	15	2	0	0	0	0	0	1	1	1	5	Drive Fault	0	0	0	1000	XAF-nnnnA	1	1	0	5	Failed to Start	0	0	0	1000	XAR-nnnn	1	1	1	5	Failed to Stop	0	0	0	1000	XAS-nnnnA	1	1	1	5	Interlock Trip	0	0	0	500	XAS-nnnnB	1	1	1	5	I/O Fault	0	0	0	1000	XAF-nnnnB	1	1	1	1	0	1	1	1	0	0	0	0	0	0	0
		MyP_PF52x	1	PF523 / PF525 Variable Frequency Drive	Motor Speed Control	P_PF52x	area01	Digital Input 1	Digital Input 2	Digital Input 3	Digital Input 4	Forward	Reverse	Hz	Hz	0	0	0	0	0	0	0	0	0	1	0	0	0	0	0	0	1	1	0	0	0	60	0	6000	0	60	2	0	6000	60	0	10	15	15	2	0	0	0	0	0	1	1	1	5	Drive Fault	0	0	0	1000	XAF-nnnnA	1	1	1	5	Failed to Start	0	0	0	1000	XAR-nnnn	1	1	1	5	Failed to Stop	0	0	0	1000	XAS-nnnnA	1	1	1	5	Interlock Trip	0	0	0	500	XAS-nnnnB	1	1	1	5	I/O Fault	0	0	0	1000	XAF-nnnnB	1	1	1	1	0	1	1	1	0	0	0	0	0	0	0
			2
			3
			4
			5
			6
			7
			8
			9
			10
			11
			12
			13
			14
			15
			16
			17
			18
			19
			20
			21
			22
			23
			24
			25
			26
			27
			28
			29
			30
			31
			32
			33
			34
			35
			36
			37
			38
			39
			40
			41
			42
			43
			44
			45
			46
			47
			48
			49
			50
			51
			52
			53
			54
			55
			56
			57
			58
			59
			60
			61
			62
			63
			64
			65
			66
			67
			68
			69
			70
			71
			72
			73
			74
			75
			76
			77
			78
			79
			80
			81
			82
			83
			84
			85
			86
			87
			88
			89
			90

## P_PF6000
	P_PF6000: PowerFlex 6000 MV Drive	Read From CLX:					i
		Send To CLX:

		Description:		Description for display on HMI	Label for graphic symbol displayed on HMI	Tagname for display on HMI	Process Area for security	Speed Reference Engineering Units for display on HMI	Speed Feedback Engineering Units for display on HMI	Speed Reference Minimum in Drive (raw) Units (for scaling)	Speed Reference Maximum in Drive (raw) Units (for scaling)	Speed Reference Minimum in Engineering Units (for scaling)	Speed Reference Maximum in Engineering Units (for scaling)	Number of decimal places for CV display (0..6)	Speed Feedback Minimum in Drive (raw) Units (for scaling)	Speed Feedback Maximum in Drive (raw) Units (for scaling)	Speed Feedback Minimum in Engineering Units (for scaling)	Speed Feedback Maximum in Engineering Units (for scaling)	1=Allow Local Start/Stop without alarm, 0=Start/Stop from HMI/prog only	Minimum Speed Reference in EU (for limiting)	Maximum Speed Reference in EU (for limiting)	Time to pulse Out_Reset to clear drive fault	Time after Start to get Run Feedback before Fault (sec)	Time after Stop to drop Run Feedback before Fault (sec)	1=Stop Motor and Alarm on Fail to Start; 0=Alarm only on Fail to Start	1=Stop Motor and Alarm on I/O Fault; 0=Alarm only on I/O Fault	1=In simulation, scale Speed Ref EU to Speed Fdbk EU	1=In simulation, scale Speed Ref EU to raw, then raw to Speed Fdbk EU	Communications Watchdog Timeout time (sec)	Time to ramp speed fdbk when in Simulation (sec)	1=Enable navigation to Parameter Read/Write Popup	1=Tells HMI a P_Perm is connected to Inp_Perm	1=Tells HMI a P_Intlk is connected to Inp_Intlk	1=Tells HMI an object with more info is available	Time to sound audible on commanded start (sec) (0=disabled)	1=Tells HMI a P_ResInh Restart Inhibit is connected	1=Tells HMI a P_RunTime is connected	Fail To Start Alarm Condition	Fail To Start Alarm Tag	1=Fail To Start Alarm exists and will be checked	1=Reset required to clear Fail To Start Alarm	1=Acknowledge required for Fail to Start Alarm	Fail To Start Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	Fail To Stop Alarm Condition	Fail To Stop Alarm Tag	1=Fail To Stop Alarm exists and will be checked	1=Reset required to clear Fail To Stop Alarm	1=Acknowledge required for Fail to Stop Alarm	Fail To Stop Alarm Severity: 1=info, 2=warn, 3=excep, 4=fault	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	Interlock Tripped Alarm Condition	Interlock Tripped Alarm Tag	1=Interlock Tripped Alarm exists and will be checked	1=Reset required to clear Interlock Trip Alarm	1=Acknowledge required for Interlock Trip Alarm	Interlock Trip Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	Drive Fault Alarm Condition	Drive Fault Alarm Tag	1=Drive Fault Alarm exists and will be checked	1=Reset required to clear Drive Fault Alarm	1=Acknowledge required for Drive Fault Alarm	Drive Fault Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	I/O Fault Alarm Condition	I/O Fault Alarm Tag	1=I/O Fault Alarm exists and will be checked	1=Reset required to clear I/O Fault Alarm	1=Acknowledge required for I/O Fault Alarm	I/O Fault Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	1=OCmd_Stop any time, 0=OCmd_Stop only when Oper selected	1=XCmd_Stop any time, 0=XCmd_Stop only when Ext selected	1=New drive OCmd resets shed latches and cleared alarms, 0=OCmdReset reqd	1=New Device XCmd resets shed latches and cleared alarms, 0=XCmdReset reqd	1=Override ignores Bypassable Perm/ Intlk; 0=always use Perm/Intlk	1=PSets track OSets in Oper, OSets track PSets in Prog, 0=no tracking	1=Prog/Oper Settings track Override/Hand speed reference	Oper keeps control in Prog Mode: .0=Reference, .1=Start/Stop	Prog keeps control in Oper Mode: .0=Reference, .1=Start/Stop	Prog keeps control in Oper Mode: .0=Reference, .1=Start/Stop, .2=Fwd/Rev	1=Operator (unlocked) exists, can be selected	1=Operator Locked exists, can be selected	1=Program (unlocked) exists, can be selected	1=Program Locked exists, can be selected	1=External exists, can be selected	1=Maintenance exists, can be selected	1=Maintenance Out of Service exists, can be selected	1=Override supersedes Prog/Oper Lock, 0=don't override Lock	1=External supersedes Prog/Oper Lock, 0=don't override Lock	1=Power Up to Prog, 0=Power Up to Oper	Normal Source: 1=Program if no requests; 0=Operator if no requests	Command Priority: 1=Program Cmds Win; 0=Operator Cmds Win	1=PCmd_Prog used as a Level (1=Prog, 0=Oper)	1=PCmd_Lock used as a Level (1=Lock, 0=Unlock)	1=XCmd_Acq used as Level (1=Acq, 0=Rel)
		Usage:		Local	Local	Local	Local	Local	Local	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Local	Local	Local	Local	Local	Local	Local	Local	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Local	Local	Local	Local	Local	Local	Local	Local
		Data Type:		STRING_40	STRING_20	STRING_20	STRING_Area	STRING_8	STRING_8	REAL	REAL	REAL	REAL	DINT	REAL	REAL	REAL	REAL	BOOL	REAL	REAL	REAL	REAL	REAL	BOOL	BOOL	BOOL	BOOL	REAL	REAL	BOOL	BOOL	BOOL	BOOL	REAL	BOOL	BOOL	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	SINT	SINT	SINT	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL
			(Origin)	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.FailToStart.Cfg_	.FailToStart.Cfg_	.FailToStart.Cfg_	.FailToStart.Cfg_	.FailToStart.Cfg_	.FailToStart.Cfg_	.FailToStart.Cfg_	.FailToStart.Cfg_	.FailToStop.Cfg_	.FailToStop.Cfg_	.FailToStop.Cfg_	.FailToStop.Cfg_	.FailToStop.Cfg_	.FailToStop.Cfg_	.FailToStop.Cfg_	.FailToStop.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.DriveFault.Cfg_	.DriveFault.Cfg_	.DriveFault.Cfg_	.DriveFault.Cfg_	.DriveFault.Cfg_	.DriveFault.Cfg_	.DriveFault.Cfg_	.DriveFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_
Unit	Tag Description	TagName	Instance	Desc	Label	Tag	Area	SpeedRefEU	SpeedFdbkEU	SpeedRefRawMin	SpeedRefRawMax	SpeedRefEUMin	SpeedRefEUMax	DecPlcs	SpeedFdbkRawMin	SpeedFdbkRawMax	SpeedFdbkEUMin	SpeedFdbkEUMax	AllowLocal	MinSpdRef	MaxSpdRef	ResetPulseT	FailToStartT	FailToStopT	ShedOnFailToStart	ShedOnIOFault	SimScaleEU	SimScaleRaw	WatchdogT	SimRampT	HasParRWObj	HasPermObj	HasIntlkObj	HasMoreObj	StartHornT	HasResInhObj	HasRunTimeObj	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	OperStopPrio	ExtStopPrio	OCmdResets	XCmdResets	OvrdPermIntlk	SetTrack	SetTrackOvrdHand	OperKeep	ProgKeep	ExtKeep	HasOper	HasOperLocked	HasProg	HasProgLocked	HasExt	HasMaint	HasMOoS	OvrdOverLock	ExtOverLock	ProgPwrUp	ProgNormal	PCmdPriority	PCmdProgAsLevel	PCmdLockAsLevel	ExtAcqAsLevel
		Default Values:	0	PowerFlex 6000 Variable Frequency Drive	Motor Speed Control	P_PF6000	area01	Hz	Hz	0	60	0	60	0	0	60	0	60	0	0	60	2	15	15	1	1	0	0	5	10	0	0	0	0	0	0	0	Failed to Start	P_PF6000.FailToStart	0	0	1	1000	0	1	5	480	Failed to Stop	P_PF6000.FailToStop	0	0	1	1000	0	1	5	480	Interlock Trip	P_PF6000.IntlkTrip	0	0	1	500	0	1	5	480	Drive Fault	P_PF6000.DriveFault	0	0	1	1000	0	1	5	480	I/O Fault	P_PF6000.IOFault	0	0	1	1000	0	1	5	480	0	0	0	0	0	1	0	0	0	0	1	1	1	1	0	1	1	1	0	0	0	0	0	0	0
		MyP_PF6000	1	PF6000 MV Variable Frequency Drive	Motor Speed Control	P_PF6000	area01	Hz	Hz	0	0	0	60	0	0	0	0	60	0	0	60	2	15	15	1	1	0	0	5	10	1	1	1	0	0	0	0	Failed to Start	XAR-nnnn	0	0	1	1000	1	1	5	0	Failed to Stop	XAS-nnnnA	0	0	1	1000	1	1	5	0	Interlock Trip	XAS-nnnnB	0	0	1	500	1	1	5	0	Drive Fault	XAF-nnnnA	0	0	1	1000	1	1	5	0	I/O Fault	XAF-nnnnB	0	0	1	1000	1	1	5	0	0	0	0	0	0	1	0	0	0	0	1	1	1	1	0	1	1	1	0	0	0	0	0	0	0
			2
			3
			4
			5
			6
			7
			8
			9
			10
			11
			12
			13
			14
			15
			16
			17
			18
			19
			20
			21
			22
			23
			24
			25
			26
			27
			28
			29
			30	Strings too long to fit are formatted like this.
	NOTE:		31
	Drive Fault Code numbers and		32
	corresponding Fault Descriptions are		33
	stored in a separate Tag. Use the Drive		34
	Fault Code sheets to read / save / restore		35
	those values.		36
			37
			38
			39
			40
			41
			42
			43
			44
			45
			46
			47
			48
			49
			50
			51
			52
			53
			54
			55
			56
			57
			58
			59
			60
			61
			62
			63
			64
			65
			66
			67
			68
			69
			70
			71
			72
			73
			74
			75
			76
			77
			78
			79
			80
			81
			82
			83
			84
			85
			86
			87
			88
			89
			90
			91
			92
			93
			94
			95
			96
			97
			98
			99

## P_PF7000
	P_PF7000: PowerFlex 7000 MV Drive	Read From CLX:
		Send To CLX:

		Description:		Description for display on HMI	Label for graphic symbol displayed on HMI	Tagname for display on HMI	Process Area for security	Name for Forward Direction, e.g., "Up", "Forward"	Name for Reverse Direction, e.g., "Down", "Reverse"	Speed Reference Engineering Units for display on HMI	Speed Feedback Engineering Units for display on HMI	Speed Reference Minimum in Drive (raw) Units (for scaling)	Speed Reference Maximum in Drive (raw) Units (for scaling)	Speed Reference Minimum in Engineering Units (for scaling)	Speed Reference Maximum in Engineering Units (for scaling)	Number of decimal places for CV display (0..6)	Speed Feedback Minimum in Drive (raw) Units (for scaling)	Speed Feedback Maximum in Drive (raw) Units (for scaling)	Speed Feedback Minimum in Engineering Units (for scaling)	Speed Feedback Maximum in Engineering Units (for scaling)	1=Drive Jog Command enabled/visible, 0=Drive Jog Command not allowed	1=Allow Local Start/Stop without alarm, 0=Start/Stop from HMI/prog only	Minimum Speed Reference in EU (for limiting)	Maximum Speed Reference in EU (for limiting)	Maximum jog time (sec, 0=unlimited)	Time to pulse Out_Reset to clear drive fault	Time after Start to get Run Feedback before Fault (sec)	Time after Stop to drop Run Feedback before Fault (sec)	1=Stop Motor and Alarm on Fail to Start; 0=Alarm only on Fail to Start	1=Stop Motor and Alarm on I/O Fault; 0=Alarm only on I/O Fault	1=In simulation, scale Speed Ref EU to Speed Fdbk EU	1=In simulation, scale Speed Ref EU to raw, then raw to Speed Fdbk EU	Time to ramp speed fdbk when in Simulation (sec)	1=Tells HMI a P_Perm is connected to Inp_FwdPerm	1=Tells HMI a P_Perm is connected to Inp_RevPerm	1=Tells HMI a P_Intlk is connected to Inp_Intlk	1=Tells HMI an object with more info is available	Time to sound audible on commanded start (sec) (0=disabled)	1=Tells HMI a P_ResInh Restart Inhibit is connected	1=Tells HMI a P_RunTime is connected	Fail To Start Alarm Condition	Fail To Start Alarm Tag	1=Fail To Start Alarm exists and will be checked	1=Reset required to clear Fail To Start Alarm	1=Acknowledge required for Fail to Start Alarm	Fail To Start Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	Fail To Stop Alarm Condition	Fail To Stop Alarm Tag	1=Fail To Stop Alarm exists and will be checked	1=Reset required to clear Fail To Stop Alarm	1=Acknowledge required for Fail to Stop Alarm	Fail To Stop Alarm Severity: 1=info, 2=warn, 3=excep, 4=fault	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	Interlock Tripped Alarm Condition	Interlock Tripped Alarm Tag	1=Interlock Tripped Alarm exists and will be checked	1=Reset required to clear Interlock Trip Alarm	1=Acknowledge required for Interlock Trip Alarm	Interlock Trip Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	Drive Fault Alarm Condition	Drive Fault Alarm Tag	1=Drive Fault Alarm exists and will be checked	1=Reset required to clear Drive Fault Alarm	1=Acknowledge required for Drive Fault Alarm	Drive Fault Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	I/O Fault Alarm Condition	I/O Fault Alarm Tag	1=I/O Fault Alarm exists and will be checked	1=Reset required to clear I/O Fault Alarm	1=Acknowledge required for I/O Fault Alarm	I/O Fault Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	1=OCmd_Stop any time, 0=OCmd_Stop only when Oper selected	1=XCmd_Stop any time, 0=XCmd_Stop only when Ext selected	1=New drive OCmd resets shed latches and cleared alarms, 0=OCmdReset reqd	1=New drive XCmd resets shed latches and cleared alarms, 0=XCmdReset reqd	1=Override ignores Bypassable Perm/ Intlk; 0=always use Perm/Intlk	1=PSets track OSets in Oper, OSets track PSets in Prog, 0=no tracking	1=Prog/Oper Settings track Override/Hand speed reference	Oper keeps control in Prog or Ext: .0=Reference, .1=Commands	Prog keeps control in Oper or Ext: .0=Reference, .1=Commands	Ext keeps control in Prog or Oper: .0=Reference, .1=Commands	1=Operator (unlocked) exists, can be selected	1=Operator Locked exists, can be selected	1=Program (unlocked) exists, can be selected	1=Program Locked exists, can be selected	1=External exists, can be selected	1=Maintenance exists, can be selected	1=Maintenance Out of Service exists, can be selected	1=Override supersedes Prog/Oper Lock, 0=don't override Lock	1=External supersedes Prog/Oper Lock, 0=don't override Lock	1=Power Up to Prog, 0=Power Up to Oper	Normal Source: 1=Program if no requests; 0=Operator if no requests	Command Priority: 1=Program Cmds Win; 0=Operator Cmds Win	1=PCmd_Prog used as a Level (1=Prog, 0=Oper)	1=PCmd_Lock used as a Level (1=Lock, 0=Unlock)	1=XCmd_Acq used as Level (1=Acq, 0=Rel)
		Usage:		Local	Local	Local	Local	Local	Local	Local	Local	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Local	Local	Local	Local	Local	Local	Local	Local	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Local	Local	Local	Local	Local	Local	Local	Local
		Data Type:		STRING_40	STRING_20	STRING_20	STRING_Area	STRING_16	STRING_16	STRING_8	STRING_8	REAL	REAL	REAL	REAL	DINT	REAL	REAL	REAL	REAL	BOOL	BOOL	REAL	REAL	REAL	REAL	REAL	REAL	BOOL	BOOL	BOOL	BOOL	REAL	BOOL	BOOL	BOOL	BOOL	REAL	BOOL	BOOL	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	SINT	SINT	SINT	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL
			(Origin)	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.FailToStart.Cfg_	.FailToStart.Cfg_	.FailToStart.Cfg_	.FailToStart.Cfg_	.FailToStart.Cfg_	.FailToStart.Cfg_	.FailToStart.Cfg_	.FailToStart.Cfg_	.FailToStop.Cfg_	.FailToStop.Cfg_	.FailToStop.Cfg_	.FailToStop.Cfg_	.FailToStop.Cfg_	.FailToStop.Cfg_	.FailToStop.Cfg_	.FailToStop.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.DriveFault.Cfg_	.DriveFault.Cfg_	.DriveFault.Cfg_	.DriveFault.Cfg_	.DriveFault.Cfg_	.DriveFault.Cfg_	.DriveFault.Cfg_	.DriveFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_
Unit	Tag Description	TagName	Instance	Desc	Label	Tag	Area	FwdText	RevText	SpeedRefEU	SpeedFdbkEU	SpeedRefRawMin	SpeedRefRawMax	SpeedRefEUMin	SpeedRefEUMax	DecPlcs	SpeedFdbkRawMin	SpeedFdbkRawMax	SpeedFdbkEUMin	SpeedFdbkEUMax	HasJog	AllowLocal	MinSpdRef	MaxSpdRef	MaxJogT	ResetPulseT	FailToStartT	FailToStopT	ShedOnFailToStart	ShedOnIOFault	SimScaleEU	SimScaleRaw	SimRampT	HasFwdPermObj	HasRevPermObj	HasIntlkObj	HasMoreObj	StartHornT	HasResInhObj	HasRunTimeObj	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	OperStopPrio	ExtStopPrio	OCmdResets	XCmdResets	OvrdPermIntlk	SetTrack	SetTrackOvrdHand	OperKeep	ProgKeep	ExtKeep	HasOper	HasOperLocked	HasProg	HasProgLocked	HasExt	HasMaint	HasMOoS	OvrdOverLock	ExtOverLock	ProgPwrUp	ProgNormal	PCmdPriority	PCmdProgAsLevel	PCmdLockAsLevel	ExtAcqAsLevel
		Default Values:	0	PowerFlex 7000 Variable Frequency Drive	Motor Speed Control	P_PF7000	area01	Forward	Reverse	Hz	Hz	0	60	0	60	2	0	60	0	60	0	0	0	60	0	2	15	15	1	1	0	0	10	0	0	0	0	0	0	0	Failed to Start	P_PF7000.FailToStart	0	0	1	1000	0	1	5	480	Failed to Stop	P_PF7000.FailToStop	0	0	1	1000	0	1	5	480	Interlock Trip	P_PF7000.IntlkTrip	0	0	1	500	0	1	5	480	Drive Fault	P_PF7000.DriveFault	0	0	1	1000	0	1	5	480	I/O Fault	P_PF7000.IOFault	0	0	1	1000	0	1	5	480	0	0	0	0	0	1	0	0	0	0	1	1	1	1	0	1	1	1	0	0	0	0	0	0	0
		MyP_PF7000	1	PowerFlex 7000 Variable Frequency Drive	Motor Speed Control	MyP_PF7000	area01	Forward	Reverse	Hz	Hz	0	32767	0	60	2	0	600	0	60	0	0	0	60	0	2	15	15	1	1	0	0	10	0	0	0	0	0	0	0	Failed to Start	XAR-nnnn	1	0	1	1000	1	1	5	0	Failed to Stop	XAS-nnnnA	1	0	1	1000	1	1	5	0	Interlock Trip	XAS-nnnnB	1	0	1	500	1	1	5	0	Drive Fault	XAF-nnnnA	1	0	1	1000	1	1	5	0	I/O Fault	XAF-nnnnB	1	0	1	1000	1	1	5	0	0	0	0	0	0	1	0	0	0	0	1	1	1	1	0	1	1	1	0	0	0	0	0	0	0
			2
			3
			4
			5
			6
			7
			8
			9
			10
			11
			12
			13
			14
			15
			16
			17
			18
			19
			20
			21
			22
			23
			24
			25
			26
			27
			28
			29
			30	Strings too long to fit are formatted like this.
			31
			32
			33
			34
			35
			36
			37
			38
			39
			40
			41
			42
			43
			44
			45
			46
			47
			48
			49
			50
			51
			52
			53
			54
			55
			56
			57
			58
			59
			60
			61
			62
			63
			64
			65
			66
			67
			68
			69
			70
			71
			72
			73
			74
			75
			76
			77
			78
			79
			80
			81
			82
			83
			84
			85
			86
			87
			88
			89
			90
			91
			92
			93
			94
			95
			96
			97
			98
			99

## P_PF753
	P_PF753: PowerFlex 753 Drive	Read From CLX:
		Send To CLX:

		Description:		Description for display on HMI	Label for graphic symbol displayed on HMI	Tagname for display on HMI	Process Area for security	Name for Forward Direction, e.g., "Up", "Forward"	Name for Reverse Direction, e.g., "Down", "Reverse"	Speed Feedback Engineering Units for display on HMI	Speed Feedback Minimum in Drive (raw) Units (for scaling)	Speed Feedback Maximum in Drive (raw) Units (for scaling)	Speed Feedback Minimum in Engineering Units (for scaling)	Speed Feedback Maximum in Engineering Units (for scaling)	Speed Reference Engineering Units for display on HMI	Speed Reference Minimum in Drive (raw) Units (for scaling)	Speed Reference Maximum in Drive (raw) Units (for scaling)	Speed Reference Minimum in Engineering Units (for scaling)	Speed Reference Maximum in Engineering Units (for scaling)	Number of decimal places for CV display (0..6)	1=Drive can be run reverse, 0=Forward only	1=Drive Jog Command enabled/visible, 0=Drive Jog Command not allowed	1=Allow Local Start/Stop without alarm, 0=Start/Stop from HMI/prog only	Minimum Speed Reference in EU (for limiting)	Maximum Speed Reference in EU (for limiting)	Maximum jog time (sec, 0=unlimited)	Time to pulse Out_Reset to clear drive fault	Time after Start to get Run Feedback before Fault (sec)	Time after Stop to drop Run Feedback before Fault (sec)	1=Stop Motor and Alarm on Fail to Start; 0=Alarm only on Fail to Start	1=Stop Motor and Alarm on I/O Fault; 0=Alarm only on I/O Fault	Time to ramp speed fdbk when in Simulation (sec)	1=In simulation, scale Speed Ref EU to Speed Fdbk EU	1=In simulation, scale Speed Ref EU to raw, then raw to Speed Fdbk EU	1=Tells HMI a P_Perm is connected to Inp_FwdPerm	1=Tells HMI a P_Perm is connected to Inp_RevPerm	1=Tells HMI a P_Intlk is connected to Inp_Intlk	Time to sound audible on commanded start (sec) (0=disabled)	1=Tells HMI a P_ResInh Restart Inhibit is connected	1=Tells HMI a P_RunTime is connected	1=Tells HMI an object with more info is available	Fail To Start Alarm Condition	Fail To Start Alarm Tag	1=Fail To Start Alarm exists and will be checked	1=Reset required to clear Fail To Start Alarm	1=Acknowledge required for Fail to Start Alarm	Fail To Start Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	Fail To Stop Alarm Condition	Fail To Stop Alarm Tag	1=Fail To Stop Alarm exists and will be checked	1=Reset required to clear Fail To Stop Alarm	1=Acknowledge required for Fail to Stop Alarm	Fail To Stop Alarm Severity: 1=info, 2=warn, 3=excep, 4=fault	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	Interlock Tripped Alarm Condition	Interlock Tripped Alarm Tag	1=Interlock Tripped Alarm exists and will be checked	1=Reset required to clear Interlock Trip Alarm	1=Acknowledge required for Interlock Trip Alarm	Interlock Trip Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	Drive Fault Alarm Condition	Drive Fault Alarm Tag	1=Drive Fault Alarm exists and will be checked	1=Reset required to clear Drive Fault Alarm	1=Acknowledge required for Drive Fault Alarm	Drive Fault Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	I/O Fault Alarm Condition	I/O Fault Alarm Tag	1=I/O Fault Alarm exists and will be checked	1=Reset required to clear I/O Fault Alarm	1=Acknowledge required for I/O Fault Alarm	I/O Fault Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	1=OCmd_Stop any time, 0=OCmd_Stop only when Oper selected	1=XCmd_Stop any time, 0=XCmd_Stop only when Ext selected	1=New drive OCmd resets shed latches and cleared alarms, 0=OCmdReset reqd	1=New drive XCmd resets shed latches and cleared alarms, 0=XCmdReset reqd	1=Override ignores Bypassable Perm/ Intlk; 0=always use Perm/Intlk	1=PSets track OSets in Oper, OSets track PSets in Prog, 0=no tracking	1=Prog/Oper Settings track Override/Hand speed reference	Oper keeps control in Prog or Ext: .0=Reference, .1=Commands	Prog keeps control in Oper or Ext: .0=Reference, .1=Commands	Ext keeps control in Prog or Oper: .0=Reference, .1=Commands	1=Operator (unlocked) exists, can be selected	1=Operator Locked exists, can be selected	1=Program (unlocked) exists, can be selected	1=Program Locked exists, can be selected	1=External exists, can be selected	1=Maintenance exists, can be selected	1=Maintenance Out of Service exists, can be selected	1=Override supersedes Prog/Oper Lock, 0=don't override Lock	1=External supersedes Prog/Oper Lock, 0=don't override Lock	1=Power Up to Prog, 0=Power Up to Oper	Normal Source: 1=Program if no requests; 0=Operator if no requests	Command Priority: 1=Program Cmds Win; 0=Operator Cmds Win	1=PCmd_Prog used as a Level (1=Prog, 0=Oper)	1=PCmd_Lock used as a Level (1=Lock, 0=Unlock)	1=XCmd_Acq used as Level (1=Acq, 0=Rel)
		Usage:		Local	Local	Local	Local	Local	Local	Local	Input	Input	Input	Input	Local	Input	Input	Input	Input	Input	Input	Input	Input	Local	Local	Local	Local	Local	Local	Local	Local	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Local	Local	Local	Local	Local	Local	Local	Local
		Data Type:		STRING_40	STRING_20	STRING_20	STRING_Area	STRING_16	STRING_16	STRING_8	DINT	DINT	REAL	REAL	STRING_8	DINT	DINT	REAL	REAL	DINT	BOOL	BOOL	BOOL	REAL	REAL	REAL	REAL	REAL	REAL	BOOL	BOOL	REAL	BOOL	BOOL	BOOL	BOOL	BOOL	REAL	BOOL	BOOL	BOOL	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	SINT	SINT	SINT	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL
			(Origin)	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.FailToStart.Cfg_	.FailToStart.Cfg_	.FailToStart.Cfg_	.FailToStart.Cfg_	.FailToStart.Cfg_	.FailToStart.Cfg_	.FailToStart.Cfg_	.FailToStart.Cfg_	.FailToStop.Cfg_	.FailToStop.Cfg_	.FailToStop.Cfg_	.FailToStop.Cfg_	.FailToStop.Cfg_	.FailToStop.Cfg_	.FailToStop.Cfg_	.FailToStop.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.DriveFault.Cfg_	.DriveFault.Cfg_	.DriveFault.Cfg_	.DriveFault.Cfg_	.DriveFault.Cfg_	.DriveFault.Cfg_	.DriveFault.Cfg_	.DriveFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_
Unit	Tag Description	TagName	Instance	Desc	Label	Tag	Area	FwdText	RevText	SpeedFdbkEU	SpeedFdbkRawMin	SpeedFdbkRawMax	SpeedFdbkEUMin	SpeedFdbkEUMax	SpeedRefEU	SpeedRefRawMin	SpeedRefRawMax	SpeedRefEUMin	SpeedRefEUMax	DecPlcs	HasReverse	HasJog	AllowLocal	MinSpdRef	MaxSpdRef	MaxJogT	ResetPulseT	FailToStartT	FailToStopT	ShedOnFailToStart	ShedOnIOFault	SimRampT	SimScaleEU	SimScaleRaw	HasFwdPermObj	HasRevPermObj	HasIntlkObj	StartHornT	HasResInhObj	HasRunTimeObj	HasMoreObj	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	OperStopPrio	ExtStopPrio	OCmdResets	XCmdResets	OvrdPermIntlk	SetTrack	SetTrackOvrdHand	OperKeep	ProgKeep	ExtKeep	HasOper	HasOperLocked	HasProg	HasProgLocked	HasExt	HasMaint	HasMOoS	OvrdOverLock	ExtOverLock	ProgPwrUp	ProgNormal	PCmdPriority	PCmdProgAsLevel	PCmdLockAsLevel	ExtAcqAsLevel
		Default Values:	0	PowerFlex 753 Variable Frequency Drive	Motor Speed Control	P_PF753	area01	Forward	Reverse	Hz	0	60000	0	60	Hz	0	60000	0	60	0	0	0	0	0	60	0	2	15	15	1	1	10	0	0	0	0	0	0	0	0	0	Failed to Start	P_PF753.FailToStart	0	0	1	1000	0	1	5	480	Failed to Stop	P_PF753.FailToStop	0	0	1	1000	0	1	5	480	Interlock Trip	P_PF753.IntlkTrip	0	0	1	500	0	1	5	480	Drive Fault	P_PF753.DriveFault	0	0	1	1000	0	1	5	480	I/O Fault	P_PF753.IOFault	0	0	1	1000	0	1	5	480	0	0	0	0	0	1	0	0	0	0	1	1	1	1	0	1	1	1	0	0	0	0	0	0	0
		MyP_PF753	1	PowerFlex 753 Variable Freq Drive	PowerFlex 753	P_PF753	area01	Forward	Reverse	Hz	0	60000	0	60	Hz	0	60000	0	60	0	0	0	0	0	60	0	2	15	15	1	1	10	0	1	1	0	1	0	1	1	0	Failed to Start	MyPF753.FailToStart	1	0	1	4	1	1	5	480	Failed to Stop	MyPF753.FailToStop	1	0	1	4	1	1	5	480	Interlock Trip	MyPF753.IntlkTrip	1	0	1	1	1	1	5	480	Drive Fault	MyPF753.DriveFault	1	0	1	4	1	1	5	480	I/O Fault	MyPF753.IOFault	1	0	1	4	1	1	5	480	0	0	0	0	0	1	0	0	0	0	1	1	1	1	0	1	1	1	0	0	0	0	0	0	0
			2
			3
			4
			5
			6
			7
			8
			9
			10
			11
			12
			13
			14
			15
			16
			17
			18
			19
			20
			21
			22
			23
			24
			25
			26
			27
			28
			29
			30	Strings too long to fit are formatted like this.
	NOTE:		31
	Drive Fault Code numbers and		32
	corresponding Fault Descriptions are		33
	stored in a separate Tag. Use the Drive		34
	Fault Code sheets to read / save / restore		35
	those values.		36
			37
			38
			39
			40
			41
			42
			43
			44
			45
			46
			47
			48
			49
			50
			51
			52
			53
			54
			55
			56
			57
			58
			59
			60
			61
			62
			63
			64
			65
			66
			67
			68
			69
			70
			71
			72
			73
			74
			75
			76
			77
			78
			79
			80
			81
			82
			83
			84
			85
			86
			87
			88
			89
			90
			91
			92
			93
			94
			95
			96
			97
			98
			99

## P_PF755
	P_PF755: PowerFlex 753 Drive	Read From CLX:
		Send To CLX:

		Description:		Description for display on HMI	Label for graphic symbol displayed on HMI	Tagname for display on HMI	Process Area for security	Name for Forward Direction, e.g., "Up", "Forward"	Name for Reverse Direction, e.g., "Down", "Reverse"	Speed Feedback Engineering Units for display on HMI	Speed Reference and Feedback Minimum in Drive Units (Hz or RPM) (for scaling)	Speed Reference and Feedback Maximum in Drive Units (Hz or RPM) (for scaling)	Number of decimal places for CV display (0..6)	Speed Reference and Feedback Minimum in Engineering Units (for scaling)	Speed Reference and Feedback Maximum in Engineering Units (for scaling)	1=Drive is a PowerFlex 755TL or TR(TotalFORCE); 0=PowerFlex755	1=Drive can be run reverse, 0=Forward only	1=Drive Jog Command enabled/visible, 0=Drive Jog Command not allowed	1=Allow Local Start/Stop without alarm, 0=Start/Stop from HMI/prog only	Minimum Speed Reference in EU (for limiting)	Maximum Speed Reference in EU (for limiting)	Maximum jog time (sec, 0=unlimited)	Time to pulse Out_Reset to clear drive fault	Time after Start to get Run Feedback before Fault (sec)	Time after Stop to drop Run Feedback before Fault (sec)	1=Stop Motor and Alarm on Fail to Start; 0=Alarm only on Fail to Start	1=Stop Motor and Alarm on I/O Fault; 0=Alarm only on I/O Fault	Time to ramp speed fdbk when in Simulation (sec)	1=Tells HMI a P_Perm is connected to Inp_FwdPerm	1=Tells HMI a P_Perm is connected to Inp_RevPerm	1=Tells HMI a P_Intlk is connected to Inp_Intlk	Time to sound audible on commanded start (sec) (0=disabled)	1=Tells HMI a P_ResInh Restart Inhibit is connected	1=Tells HMI a P_RunTime is connected	1=Tells HMI an object with more info is available	Fail To Start Alarm Condition	Fail To Start Alarm Tag	1=Fail To Start Alarm exists and will be checked	1=Reset required to clear Fail To Start Alarm	1=Acknowledge required for Fail to Start Alarm	Fail To Start Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	Fail To Stop Alarm Condition	Fail To Stop Alarm Tag	1=Fail To Stop Alarm exists and will be checked	1=Reset required to clear Fail To Stop Alarm	1=Acknowledge required for Fail to Stop Alarm	Fail To Stop Alarm Severity: 1=info, 2=warn, 3=excep, 4=fault	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	Interlock Tripped Alarm Condition	Interlock Tripped Alarm Tag	1=Interlock Tripped Alarm exists and will be checked	1=Reset required to clear Interlock Trip Alarm	1=Acknowledge required for Interlock Trip Alarm	Interlock Trip Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	Drive Fault Alarm Condition	Drive Fault Alarm Tag	1=Drive Fault Alarm exists and will be checked	1=Reset required to clear Drive Fault Alarm	1=Acknowledge required for Drive Fault Alarm	Drive Fault Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	I/O Fault Alarm Condition	I/O Fault Alarm Tag	1=I/O Fault Alarm exists and will be checked	1=Reset required to clear I/O Fault Alarm	1=Acknowledge required for I/O Fault Alarm	I/O Fault Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	1=OCmd_Stop any time, 0=OCmd_Stop only when Oper selected	1=XCmd_Stop any time, 0=XCmd_Stop only when Ext selected	1=New drive OCmd resets shed latches and cleared alarms, 0=OCmdReset reqd	1=New drive XCmd resets shed latches and cleared alarms, 0=XCmdReset reqd	1=Override ignores Bypassable Perm/ Intlk; 0=always use Perm/Intlk	1=PSets track OSets in Oper, OSets track PSets in Prog, 0=no tracking	1=Prog/Oper Settings track Override/Hand speed reference	Oper keeps control in Prog or Ext: .0=Reference, .1=Commands	Prog keeps control in Oper or Ext: .0=Reference, .1=Commands	Ext keeps control in Prog or Oper: .0=Reference, .1=Commands	1=Operator (unlocked) exists, can be selected	1=Operator Locked exists, can be selected	1=Program (unlocked) exists, can be selected	1=Program Locked exists, can be selected	1=External exists, can be selected	1=Maintenance exists, can be selected	1=Maintenance Out of Service exists, can be selected	1=Override supersedes Prog/Oper Lock, 0=don't override Lock	1=External supersedes Prog/Oper Lock, 0=don't override Lock	1=Power Up to Prog, 0=Power Up to Oper	Normal Source: 1=Program if no requests; 0=Operator if no requests	Command Priority: 1=Program Cmds Win; 0=Operator Cmds Win	1=PCmd_Prog used as a Level (1=Prog, 0=Oper)	1=PCmd_Lock used as a Level (1=Lock, 0=Unlock)	1=XCmd_Acq used as Level (1=Acq, 0=Rel)
		Usage:		Local	Local	Local	Local	Local	Local	Local	Input	Input	Input	Input	Input	Input	Input	Input	Local	Local	Local	Local	Local	Local	Local	Local	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Local	Local	Local	Local	Local	Local	Local	Local
		Data Type:		STRING_40	STRING_20	STRING_20	STRING_Area	STRING_16	STRING_16	STRING_8	REAL	REAL	DINT	REAL	REAL	BOOL	BOOL	BOOL	BOOL	REAL	REAL	REAL	REAL	REAL	REAL	BOOL	BOOL	REAL	BOOL	BOOL	BOOL	REAL	BOOL	BOOL	BOOL	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	SINT	SINT	SINT	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL
			(Origin)	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.FailToStart.Cfg_	.FailToStart.Cfg_	.FailToStart.Cfg_	.FailToStart.Cfg_	.FailToStart.Cfg_	.FailToStart.Cfg_	.FailToStart.Cfg_	.FailToStart.Cfg_	.FailToStop.Cfg_	.FailToStop.Cfg_	.FailToStop.Cfg_	.FailToStop.Cfg_	.FailToStop.Cfg_	.FailToStop.Cfg_	.FailToStop.Cfg_	.FailToStop.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.DriveFault.Cfg_	.DriveFault.Cfg_	.DriveFault.Cfg_	.DriveFault.Cfg_	.DriveFault.Cfg_	.DriveFault.Cfg_	.DriveFault.Cfg_	.DriveFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_
Unit	Tag Description	TagName	Instance	Desc	Label	Tag	Area	FwdText	RevText	SpeedFdbkEU	SpeedRawMin	SpeedRawMax	DecPlcs	SpeedEUMin	SpeedEUMax	PF755T	HasReverse	HasJog	AllowLocal	MinSpdRef	MaxSpdRef	MaxJogT	ResetPulseT	FailToStartT	FailToStopT	ShedOnFailToStart	ShedOnIOFault	SimRampT	HasFwdPermObj	HasRevPermObj	HasIntlkObj	StartHornT	HasResInhObj	HasRunTimeObj	HasMoreObj	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	OperStopPrio	ExtStopPrio	OCmdResets	XCmdResets	OvrdPermIntlk	SetTrack	SetTrackOvrdHand	OperKeep	ProgKeep	ExtKeep	HasOper	HasOperLocked	HasProg	HasProgLocked	HasExt	HasMaint	HasMOoS	OvrdOverLock	ExtOverLock	ProgPwrUp	ProgNormal	PCmdPriority	PCmdProgAsLevel	PCmdLockAsLevel	ExtAcqAsLevel
		Default Values:	0	PowerFlex 755 Variable Frequency Drive	Motor Speed Control	P_PF755	area01	Forward	Reverse	Hz	0	60000	2	0	60	0	0	0	0	0	60	0	2	15	15	1	1	10	0	0	0	0	0	0	0	Failed to Start	P_PF755.FailToStart	0	0	1	1000	0	1	5	480	Failed to Stop	P_PF755.FailToStop	0	0	1	1000	0	1	5	480	Interlock Trip	P_PF755.IntlkTrip	0	0	1	500	0	1	5	480	Drive Fault	P_PF755.DriveFault	0	0	1	1000	0	1	5	480	I/O Fault	P_PF755.IOFault	0	0	1	1000	0	1	5	480	0	0	0	0	0	1	0	0	0	0	1	1	1	1	0	1	1	1	0	0	0	0	0	0	0
		MyP_PF755	1	PowerFlex 755 Variable Frequency Drive	Motor Speed Control	P_PF755	area01	Forward	Reverse	Hz	0	60	2	0	60	0	0	0	0	0	60	0	2	15	15	1	1	10	1	0	1	0	1	1	0	Failed to Start	XAR-nnnn	1	0	1	3	1	1	5	480	Failed to Stop	XAS-nnnnA	1	0	1	3	1	1	5	480	Interlock Trip	XAS-nnnnB	1	0	1	3	1	1	5	480	Drive Fault	XAF-nnnnA	1	0	1	3	1	1	5	480	I/O Fault	XAF-nnnnB	1	0	1	3	1	1	5	480	0	0	0	0	0	1	0	0	0	0	1	1	1	1	0	1	1	1	0	0	0	0	0	0	0
			2
			3
			4
			5
			6
			7
			8
			9
			10
			11
			12
			13
			14
			15
			16
			17
			18
			19
			20
			21
			22
			23
			24
			25
			26
			27
			28
			29
			30	Strings too long to fit are formatted like this.
	NOTE:		31
	Drive Fault Code numbers and		32
	corresponding Fault Descriptions are		33
	stored in a separate Tag. Use the Drive		34
	Fault Code sheets to read / save / restore		35
	those values.		36
			37
			38
			39
			40
			41
			42
			43
			44
			45
			46
			47
			48
			49
			50
			51
			52
			53
			54
			55
			56
			57
			58
			59
			60
			61
			62
			63
			64
			65
			66
			67
			68
			69
			70
			71
			72
			73
			74
			75
			76
			77
			78
			79
			80
			81
			82
			83
			84
			85
			86
			87
			88
			89
			90
			91
			92
			93
			94
			95
			96
			97
			98
			99

## P_PIDE
	P_PIDE: Enhanced PID	Read From CLX:
		Send To CLX:

		Description:		Description for display on HMI	Label for graphic symbol displayed on HMI	Tagname for display on HMI	Process Area for security	PV / Setpoint Engineering Units displayed on HMI	PV Engineering Units Mimimum Value (PVEU)	PV Engineering Units Maximum Value (PVEU)	Number of decimal places for PV display (0..6)	CV Engineering Units displayed on HMI	CV Engineering Units Minimum Value (CVEU)	CV Engineering Units Maximum Value (CVEU)	CV Output Units Minimum Value (CVRaw, for scaling))	CV Output Units Maximum Value (CVRaw, for scaling))	Number of decimal places for display of CV (0..6)	Execution Time (interval) for PID Algorithm (sec)	1=Casc Loop Mode is Ratio, 0=Casc Loop Mode is Cascade	1=Enable the loop to be placed into cascade/ratio mode	1=Enable the loop to be placed into automatic mode	1=Enable the loop to be placed into manual mode	1=Enable the Setpoint Ramp 'Wizard' function	1=SP tracks PV in Manual, 0=no PV tracking	1=Direct acting (E=PV-SP), 0=Reverse acting (E=SP-PV)	1=Dependent gains equation, 0=Independent gains	1=Use Derivative Smoothing	1=need not cross zero error to be in deadband, 0=must cross zero error	1=CV limits enforced in Manual, 0=No CV Limiting in Manual	1=Go to Manual Loop Mode when an init request is seen	Proportional Action on SP Change 1= None (PV only), 0= Full (Loop Error)	Derivative Action on SP Change 1=None (PV only), 0=Full (Loop Error)	1=Latch in Interlock shed action until Reset 0=Return when Interlock clears	1=Latch in SP Fail shed action until Reset 0=Return when SP is good	1=Latch in PV Fail shed action until Reset 0=Return when PV is good	1=Latch in CV Fail shed action until Reset 0=Return when CV is good	Interlock Trip Setpoint Action: 0=none, 1=hold last good, 2=use Cfg_IntlkSP, 3= set SP to curr. PV	SP Fail Setpoint Action: 1=hold last good, 2=use Cfg_IntlkSP, 3= set SP to curr. PV	PV Fail Setpoint Action: 0=none, 1=hold last good, 2=use Cfg_IntlkSP	CV Fail Setpoint Action: 0=none, 1=hold last good, 2=use Cfg_IntlkSP, 3= set SP to curr. PV	Interlock Trip CV Action: 0=none, 1=hold last good, 2=use Cfg_IntlkCV	SP Fail CV Action: 0=none, 1=hold last good, 2=use Cfg_IntlkCV	PV Fail CV Action: 1=hold last good, 2=use Cfg_IntlkCV	PV Fail CV Action: 1=hold last good, 2=use Cfg_IntlkCV	Interlock Trip Loop Mode Action: 0=none, 1=Man only, 2=Auto or Man only	SP Fail Loop Mode Action: 0=none, 1=Man only, 2=Auto or Man only	PV Fail Loop Mode Action: 0=none, 1=Man only, 2=Auto or Man only	CV Fail Loop Mode Action: 0=none, 1=Man only, 2=Auto or Man only	Proportional (independent) or Loop (dependent) Gain (unitless)	Integral Gain (1/min independent or min/repeat dependent)	Derivative Gain (min)	Normal Zero Crossing Deadband (PVEU)	Minimum allowed Ratio (unitless)	Maximum allowed Ratio (unitless)	Minimum allowed Setpoint (SP) value (PVEU)	Maximum allowed Setpoint (SP) value (PVEU)	Minimum allowed Controlled Variable (CV) value (CVEU)	Maximum allowed Controlled Variable (CV) value (CVEU)	When Val_CV is greater than this value (in CV EU) set Sts_Active (for HMI)	Maximum allowed Setpoint (SP) value (PVEU)	Maximum allowed Setpoint (SP) value (PVEU)	CV Rate of Change Limit (CV%/sec)	CV Rate of Change Limit (CV%/sec)			Powerup Loop Mode 0=No change (last), 1=Man (w/ CV), 2=Auto (w/ SP), 3=Casc, 4=Normal	Loop SP on powerup, used if Cfg_PwrupLM = 1 (Manual) or 2 (Auto)	Loop CV on powerup, used if Cfg_PwrupLM <> 0 (none)		Current High Deviation Status Threshold	High Deviation Status Deadband (EU)	Current High Deviation Status Threshold	High Deviation Status Deadband (EU)	Current Low Deviation Status Threshold	Low Deviation Status Deadband (EU)	Current Low Deviation Status Threshold	Low Deviation Status Deadband (EU)	CV Value to use with Interlock / Bad Value CV action	SP Value to use with Interlock / Bad Value SP action	1=Tells HMI a P_Intlk is connected to Inp_Intlk	1=Tells HMI an object with more info is available	1=Tells HMI to enable navigation to a connected cascade SP object	Tagname for destination of Cascade SP Navigation button	1=Tells HMI to enable navigation to a connected PV object	Tagname for destination of PV Navigation button	1=Tells HMI to enable navigation to a connected CV object	Tagname for destination of CV Navigation button	High-High Deviation Status Input Condition	High-High Deviation Status Gate Condition	High-High Deviation Status Gate Delay (s)	Minimum time above High-High Deviation Limit to raise Status (sec)	Minimum time below High-High Deviation Limit (minus deadband) to clear Status (sec)	High-High Deviation Alarm Condition	High-High Deviation Alarm Tag	1=High-High Deviation Alarm exists and will be checked	1=Reset required to clear High-High Deviation Alarm	1=Acknowledge required for High-High Deviation Alarm	High-High Deviation Alarm Severity 1=info, 2=warn, 3=excep, 4=fault	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	High Deviation Status Input Condition	High Deviation Status Gate Condition	High Deviation Status Gate Delay (s)	Minimum time above High Deviation Limit to raise Status (sec)	Minimum time below High Deviation Limit (minus deadband) to clear Status (sec)	High Deviation Alarm Condition	High Deviation Alarm Tag	1=High Deviation Alarm exists and will be checked	1=Reset required to clear High Deviation Alarm	1=Acknowledge required for High Deviation Alarm	High Deviation Alarm Severity 1=info, 2=warn, 3=excep, 4=fault	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	Low Deviation Status Input Condition	Low Deviation Status Gate Condition	Low Deviation Status Gate Delay (s)	Minimum time above Low Deviation Limit to raise Status (sec)	Minimum time below Low Deviation Limit (minus deadband) to clear Status (sec)	Low Deviation Alarm Condition	Low Deviation Alarm Tag	1=Low Deviation Alarm exists and will be checked	1=Reset required to clear Low Deviation Alarm	1=Acknowledge required for Low Deviation Alarm	Low Deviation Alarm Severity 1=info, 2=warn, 3=excep, 4=fault	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	Low-Low Deviation Status Input Condition	Low-Low Deviation Status Gate Condition	Low-Low Deviation Status Gate Delay (s)	Minimum time above Low-Low Deviation Limit to raise Status (sec)	Minimum time below Low-Low Deviation Limit (minus deadband) to clear Status (sec)	Low-Low Deviation Alarm Condition	Low-Low Deviation Alarm Tag	1=Low-Low Deviation Alarm exists and will be checked	1=Reset required to clear Low-Low Deviation Alarm	1=Acknowledge required for Low-Low Deviation Alarm	Low-Low Deviation Alarm Severity 1=info, 2=warn, 3=excep, 4=fault	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	Interlock Tripped Alarm Condition	Interlock Tripped Alarm Tag	1=Interlock Tripped Alarm exists and will be checked	1=Interlock Tripped Alarm is latched in, requires Reset Command to clear	1=Interlock Tripped Alarm must be acknowledged	Interlock Tripped Alarm Severity: 1=info, 2=warn, 3=excep, 4=fault	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	Loop Failure Alarm Condition	Loop Failure Alarm Tag	1=Loop Failure Alarm exists and will be checked	1=Loop Failure Alarm is latched in, requires Reset Command to clear	1=Loop Failure Alarm must be acknowledged	Loop Failure Alarm Severity: 1=info, 2=warn, 3=excep, 4=fault	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	1=PSets track OSets in Oper, OSets track PSets in Prog, 0=no tracking	1=Prog/Oper Settings track Override/Hand Inputs (CV, SP, Ratio)	1=Override ignores Bypassable Intlk; 0=always use Intlk	Oper keeps control in Prog or Ext: .0=Reference, .1=Commands	Prog keeps control in Oper or Ext: .0=Reference, .1=Commands	Ext keeps control in Prog or Oper: .0=Reference, .1=Commands	1=Operator (unlocked) exists, can be selected	1=Operator Locked exists, can be selected	1=Program (unlocked) exists, can be selected	1=Program Locked exists, can be selected	1=External exists, can be selected	1=Maintenance exists, can be selected	1=Maintenance Out of Service exists, can be selected	1=Override supersedes Prog/Oper Lock, 0=don't override Lock	1=External supersedes Prog/Oper Lock, 0=don't override Lock	1=Power Up to Prog, 0=Power Up to Oper	Normal Source: 1=Program if no requests; 0=Operator if no requests	Command Priority: 1=Program Cmds Win; 0=Operator Cmds Win	1=PCmd_Prog used as a Level (1=Prog, 0=Oper)	1=PCmd_Lock used as a Level (1=Lock, 0=Unlock)	1=XCmd_Acq used as Level (1=Acq, 0=Rel)
		Usage:		Local	Local	Local	Local	Local	Input	Input	Input	Local	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Local	Input	Local	Input	Local	Local	Local	Local	Local	Local	Local	Local	Input	Input	Input	Input	Input	Input	Local	Local	Local	Local	Local	Local	Local	Local	Input	Input	Input	Input
		Data Type:		STRING_40	STRING_20	STRING_20	STRING_Area	STRING_8	REAL	REAL	DINT	STRING_8	REAL	REAL	REAL	REAL	DINT	REAL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	DINT	DINT	DINT	DINT	DINT	DINT	DINT	DINT	REAL	REAL	REAL	REAL	REAL	REAL	REAL	REAL	REAL	REAL	REAL	REAL	REAL	REAL	BOOL	DINT	BOOL	DINT	REAL	REAL	REAL	REAL	REAL	REAL	REAL	REAL	REAL	REAL	BOOL	BOOL	BOOL	STRING_NavTag	BOOL	STRING_NavTag	BOOL	STRING_NavTag	STRING_20	STRING_20	REAL	REAL	REAL	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	REAL	REAL	REAL	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	REAL	REAL	REAL	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	REAL	REAL	REAL	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	BOOL	BOOL	BOOL	SINT	SINT	SINT	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL
			(Origin)	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.HiHiDevGate.Cfg_	.HiHiDevGate.Cfg_	.HiHiDevGate.Cfg_	.HiHiDevGate.Cfg_	.HiHiDevGate.Cfg_	.HiHiDev.Cfg_	.HiHiDev.Cfg_	.HiHiDev.Cfg_	.HiHiDev.Cfg_	.HiHiDev.Cfg_	.HiHiDev.Cfg_	.HiHiDev.Cfg_	.HiHiDev.Cfg_	.HiDevGate.Cfg_	.HiDevGate.Cfg_	.HiDevGate.Cfg_	.HiDevGate.Cfg_	.HiDevGate.Cfg_	.HiDev.Cfg_	.HiDev.Cfg_	.HiDev.Cfg_	.HiDev.Cfg_	.HiDev.Cfg_	.HiDev.Cfg_	.HiDev.Cfg_	.HiDev.Cfg_	.LoDevGate.Cfg_	.LoDevGate.Cfg_	.LoDevGate.Cfg_	.LoDevGate.Cfg_	.LoDevGate.Cfg_	.LoDev.Cfg_	.LoDev.Cfg_	.LoDev.Cfg_	.LoDev.Cfg_	.LoDev.Cfg_	.LoDev.Cfg_	.LoDev.Cfg_	.LoDev.Cfg_	.LoLoDevGate.Cfg_	.LoLoDevGate.Cfg_	.LoLoDevGate.Cfg_	.LoLoDevGate.Cfg_	.LoLoDevGate.Cfg_	.LoLoDev.Cfg_	.LoLoDev.Cfg_	.LoLoDev.Cfg_	.LoLoDev.Cfg_	.LoLoDev.Cfg_	.LoLoDev.Cfg_	.LoLoDev.Cfg_	.LoLoDev.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.Fail.Cfg_	.Fail.Cfg_	.Fail.Cfg_	.Fail.Cfg_	.Fail.Cfg_	.Fail.Cfg_	.Fail.Cfg_	.Fail.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_
Unit	Tag Description	TagName	Instance	Desc	Label	Tag	Area	PVEU	PVEUMin	PVEUMax	PVDecPlcs	CVEU	CVEUMin	CVEUMax	CVRawMin	CVRawMax	CVDecPlcs	ExecT	HasRatio	HasCasc	HasAuto	HasMan	HasSPRamp	PVTrack	CtrlAction	Depend	DerivSmooth	ZCOff	LimitManCV	InitToMan	PropSPAct	DerivSPAct	IntlkTripLatch	SPFailLatch	PVFailLatch	CVFailLatch	IntlkTripSPAct	SPFailSPAct	PVFailSPAct	CVFailSPAct	IntlkTripCVAct	SPFailCVAct	PVFailCVAct	CVFailCVAct	IntlkTripLMAct	SPFailLMAct	PVFailLMAct	CVFailLMAct	PGain	IGain	DGain	ZCDB	MinRatio	MaxRatio	MinSP	MaxSP	MinCV	MaxCV	MaxInactiveCV	MaxSPRoCDec	MaxSPRoCInc	CVRoCLim	SkipSPRoCLim	NormLM	LockLM	PwrupLM	PwrupSP	PwrupCV	SPRampMaxDev	HiHiDevLim	HiHiDevDB	HiDevLim	HiDevDB	LoDevLim	LoDevDB	LoLoDevLim	LoLoDevDB	IntlkCV	IntlkSP	HasIntlkObj	HasMoreObj	HasCascSPNav	CascSPNavTag	HasPVNav	PVNavTag	HasCVNav	CVNavTag	InpCond	GateCond	GateDly	OnDly	OffDly	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	InpCond	GateCond	GateDly	OnDly	OffDly	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	InpCond	GateCond	GateDly	OnDly	OffDly	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	InpCond	GateCond	GateDly	OnDly	OffDly	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	SetTrack	SetTrackOvrdHand	OvrdIntlk	OperKeep	ProgKeep	ExtKeep	HasOper	HasOperLocked	HasProg	HasProgLocked	HasExt	HasMaint	HasMOoS	OvrdOverLock	ExtOverLock	ProgPwrUp	ProgNormal	PCmdPriority	PCmdProgAsLevel	PCmdLockAsLevel	ExtAcqAsLevel
		Default Values:	0	PID Control Loop	PID Control Loop	P_PIDE	area01	'%'	0	100	2	'%'	0	100	0	100	0	0	0	0	1	1	0	0	0	0	0	0	0	0	1	0	0	2	1	1	1	0	0	0	0	0	0	0	0	1	1	0	100	0	100	0	0	0	0	0	0	0	0	0	0	0	1.50E+38	0	1.50E+38	0	-1.50E+38	0	-1.50E+38	0	0	0	0	0	0	''	0	''	0	''	Hi-Hi Deviation	Hi-Hi Deviation Gate	0	0	0	Hi-Hi Deviation	P_PIDE.HiHiDev	0	0	1	750	1	1	5	480	High Deviation	High Deviation Gate	0	0	0	High Deviation	P_PIDE.HiDev	0	0	1	500	1	1	5	480	Low Deviation	Low Deviation Gate	0	0	0	Low Deviation	P_PIDE.LoDev	0	0	1	500	1	1	5	480	Lo-Lo Deviation	Lo-Lo Deviation Gate	0	0	0	Lo-Lo Deviation	P_PIDE.LoLoDev	0	0	1	750	1	1	5	480	Interlock Trip	P_PIDE.IntlkTrip	0	0	1	500	0	1	5	480	Loop Failure	P_PIDE.Fail	0	0	1	1000	1	1	5	480	1	0	0	0	0	0	1	1	1	1	0	1	1	1	0	0	0	0	0	0	0
		MyP_PIDE	1	Reboiler Steam Flow Control	Reboiler Steam Flow	FIC_1305	area01	SCFM	0	100	2	%	0	100	0	100	2	0	1	1	1	1	0	0	0	0	0	0	0	0	1	0	0	2	1	1	1	0	0	0	0	1.39999997615814	19	0.00150000001303852	0	0.100000001490116	10	0	100	0	100	0.5	0	0	5	0	0	0	2	20	50	0	1.50000000274888E+038	0	1.50000000274888E+038	0	-1.50E+38	0	-1.50E+38	0	0	0	0	0	0		0		0		Hi-Hi Deviation	Hi-Hi Deviation Gate	0	0	0	Deviation High-High	MyP_PIDE.HiHiDev	1	0	1	3	1	1	5	480	High Deviation	High Deviation Gate	0	0	0	Deviation High	MyP_PIDE.HiDev	1	0	1	2	1	1	5	480	Low Deviation	Low Deviation Gate	0	0	0	Deviation Low	MyP_PIDE.LoDev	1	0	1	2	1	1	5	480	Lo-Lo Deviation	Lo-Lo Deviation Gate	0	0	0	Deviation Low-Low	MyP_PIDE.LoLoDev	1	0	1	3	1	1	5	480	Interlock Trip	MyP_PIDE.IntlkTrip	1	0	1	3	1	1	5	480	Loop Failure	MyP_PIDE.Fail	1	0	0	4	1	1	5	480	1	0	0	0	0	0	1	1	1	1	0	1	1	1	0	0	0	0	0	0	0
			2
			3
			4
			5
			6
			7
			8
			9
			10
			11
			12
			13
			14
			15
			16
			17
			18
			19
			20
			21
			22
			23
			24
			25
			26
			27
			28
			29
			30
			31
			32
			33
			34
			35
			36
			37
			38
			39
			40
			41
			42
			43
			44
			45
			46
			47
			48
			49
			50

## P_PTComp
	P_PTComp: Press / Temp Compensator	Read From CLX:
		Send To CLX:

		Description:		Description for display on HMI	Label for graphic symbol displayed on HMI	Tagname for display on HMI	Process Area for security	If Out_Flow is less than this cutoff value, it is shown as 0.0	Standard Temperature in Inp_T_Act units (e.g., F or C)	Standard Pressure in Inp_P_Act units (e.g., PSIG)	Zero input-units Temperature in absolute units (e.g., R or K)	Zero input-units Pressure in Absolute units (e.g., PSIA)	1=Use Inp_DP_Act (sq.rt. curve) to calculate flow, 0=Use Inp_F_Act (linear)	Reference (full- scale) Differential Pressure (e.g., "WC)	Reference Flow in volumetric units (e.g., CFM) at Reference DP	1=Tells HMI an object with more info is available
		Usage:		Local	Local	Local	Local	Input	Input	Input	Input	Input	Input	Input	Input
		Data Type:		STRING_40	STRING_20	STRING_20	STRING_Area	REAL	REAL	REAL	REAL	REAL	BOOL	REAL	REAL	BOOL
			(Origin)	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_
Unit	Tag Description	TagName	Instance	Desc	Label	Tag	Area	LoFlowCutoff	T_Std	P_Std	T_Offset	P_Offset	UseDP	DP_Ref	F_Ref	HasMoreObj
		Default Values:	0	Pressure / Temperature Compensated Flow	Flow at Std. Cond.	P_PTComp	area01	0.0	0.0	0.0	273.15	14.696	0	100.0	1.0	0
		MyP_PTComp	1	Pressure / Temperature Compensated Flow	Flow at Std. Cond.	P_PTComp	area01	0	0	0	273.149993896484	14.6960000991821	0	100	1	0
			2
			3
			4
			5
			6
			7
			8
			9
			10
			11
			12
			13
			14
			15
			16
			17
			18
			19
			20
			21
			22
			23
			24
			25
			26
			27
			28
			29
			30	Strings too long to fit are formatted like this.
			31
			32
			33
			34
			35
			36
			37
			38
			39
			40
			41
			42
			43
			44
			45
			46
			47
			48
			49
			50
			51
			52
			53
			54
			55
			56
			57
			58
			59
			60
			61
			62
			63
			64
			65
			66
			67
			68
			69
			70
			71
			72
			73
			74
			75
			76
			77
			78
			79
			80
			81
			82
			83
			84
			85
			86
			87
			88
			89
			90
			91
			92
			93
			94
			95
			96
			97
			98
			99

## P_Reset
	P_Reset: Shared Reset	Read From CLX:
		Send To CLX:

		Description:		Description for display on HMI	Label for graphic symbol displayed on HMI	Tagname for display on HMI	Process Area for security	Minimum Time to hold Reset Output true (sec)	1=Tells HMI an object with more info is available
		Usage:		Local	Local	Local	Local	Input	Input
		Data Type:		STRING_40	STRING_20	STRING_20	STRING_Area	REAL	BOOL
			(Origin)	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_
Unit	Tag Description	TagName	Instance	Desc	Label	Tag	Area	MinHoldTime	HasMoreObj
		Default Values:	0	Multiple-Device Reset	Reset	P_Reset	area01	1	0
		P1_Reset	1	Multiple-Device Reset	Reset	P_Reset	area01	2	0
			2
			3
			4
			5
			6
			7
			8
			9
			10
			11
			12
			13
			14
			15
			16
			17
			18
			19
			20
			21
			22
			23
			24
			25
			26
			27
			28
			29
			30	Strings too long to fit are formatted like this.
			31
			32
			33
			34
			35
			36
			37
			38
			39
			40
			41
			42
			43
			44
			45
			46
			47
			48
			49
			50
			51
			52
			53
			54
			55
			56
			57
			58
			59
			60
			61
			62
			63
			64
			65
			66
			67
			68
			69
			70
			71
			72
			73
			74
			75
			76
			77
			78
			79
			80
			81
			82
			83
			84
			85
			86
			87
			88
			89
			90
			91
			92
			93
			94
			95
			96
			97
			98
			99

## P_ResInh
	P_ResInh: Restart Inhibit	Read From CLX:
		Send To CLX:

		Description:		Description for display on HMI	Label for graphic symbol displayed on HMI	Tagname for display on HMI	Process Area for security	Time within which three starts are allowed if cold (hr)	Time for cold motor to wait after 1st and start failure before ready (hr)	Time for cold motor to wait after 2nd and subsequent start failure before ready (hr)	Time for hot motor to wait after 1st and start failure before ready (hr)	Time for hot motor to wait after 2nd and subsequent start failure before ready (hr)	Time for hot motor to run so it can immediately restart after stop (hr)	Time for hot motor to wait after stop if stopped before Hot Restart OK time (hr)	Time for a stopped hot motor to become cold (hr)	1=Tells HMI an object with more info is available
		Usage:		Local	Local	Local	Local	Input	Input	Input	Input	Input	Input	Input	Input
		Data Type:		STRING_40	STRING_20	STRING_20	STRING_Area	REAL	REAL	REAL	REAL	REAL	REAL	REAL	REAL	BOOL
			(Origin)	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_
Unit	Tag Description	TagName	Instance	Desc	Label	Tag	Area	ThreeColdStarts	FirstFailCold	SubseqFailCold	FirstFailHot	SubseqFailHot	HotRestartOK	RestartHot	HotToCold	HasMoreObj
		Default Values:	0	Restart Inhibit	Restart Inhibit	P_ResInh	area01	0.5	0.5	4.0	0.5	4	1	1	16	0
		MyP_Motor_ResInh	1	Restart Inhibit	Restart Inhibit	P101_Motor_ResInh	area01	0.5	0.5	4	0.5	4	1	1	16	0
			2
			3
			4
			5
			6
			7
			8
			9
			10
			11
			12
			13
			14
			15
			16
			17
			18
			19
			20
			21
			22
			23
			24
			25
			26
			27
			28
			29
			30	Strings too long to fit are formatted like this
			31
			32
			33
			34
			35
			36
			37
			38
			39
			40
			41
			42
			43
			44
			45
			46
			47
			48
			49
			50
			51
			52
			53
			54
			55
			56
			57
			58
			59
			60
			61
			62
			63
			64
			65
			66
			67
			68
			69
			70
			71
			72
			73
			74
			75
			76
			77
			78
			79
			80
			81
			82
			83
			84
			85
			86
			87
			88
			89
			90
			91
			92
			93
			94
			95
			96
			97
			98
			99

## P_RunTime
	P_RunTime: Run Time and Starts	Read From CLX:
		Send To CLX:

		Description:		Description for display on HMI	Label for graphic symbol displayed on HMI	Tagname for display on HMI	Process Area for security	1=Tells HMI an object with more info is available
		Usage:		Local	Local	Local	Local	Input
		Data Type:		STRING_40	STRING_20	STRING_20	STRING_Area	BOOL
			(Origin)	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_
Unit	Tag Description	TagName	Instance	Desc	Label	Tag	Area	HasMoreObj
		Default Values:	0	Accumulated Run Time (Hours)	Run Time	P_RunTime	area01	0
		MyP_Motor_RunTime	1	Accumulated Run Time (Hours)	Run Time	P101_Motor_RunTime	area01	0
			2
			3
			4
			5
			6
			7
			8
			9
			10
			11
			12
			13
			14
			15
			16
			17
			18
			19
			20
			21
			22
			23
			24
			25
			26
			27
			28
			29
			30	Strings too long to fit are formatted like this
			31
			32
			33
			34
			35
			36
			37
			38
			39
			40
			41
			42
			43
			44
			45
			46
			47
			48
			49
			50
			51
			52
			53
			54
			55
			56
			57
			58
			59
			60
			61
			62
			63
			64
			65
			66
			67
			68
			69
			70
			71
			72
			73
			74
			75
			76
			77
			78
			79
			80
			81
			82
			83
			84
			85
			86
			87
			88
			89
			90
			91
			92
			93
			94
			95
			96
			97
			98
			99

## P_SMC50
	P_SMC50: SMC-50 Smart Motor Controller	Read From CLX:
		Send To CLX:

		Description:		Description for display on HMI	Tagname for display on HMI	Label for graphic symbol displayed on HMI	Process Area for security	1=Motor Job Command enabled/visible, 0=Motor Jog Command not allowed	1=Allow Local Start/Stop without alarm, 0=Start/Stop from HMI/prog only	1=Tells HMI a P_Perm is connected to Inp_Perm...	1=Tells HMI a P_Intlk is connected to Inp_Intlk	1=Tells HMI an object with more info is available	Maximum jog time (sec, 0=unlimited)	Time to sound audible on commanded start (sec) (0=disabled)	1=Tells HMI a P_ResInh Restart Inhibit is connected	1=Tells HMI a P_RunTime is connected	1=OCmd_Stop has priority, accepted any time, 0=OCmd_Stop only in Oper, Maint Mode.	1=XCmd_St0 any time, 0=XCmd_St0 only when Ext selected	1=New motor OCmd resets shed latches and cleared alarms, 0=OCmdReset reqd	1=New motor XCmd resets shed latches and cleared alarms, 0=XCmdReset reqd	1=Override ignores Bypassable Perm/ Intlk; 0=always use Perm/Intlk	1=Stop Motor and Alarm on Fail to Start; 0=Alarm only on Fail to Start	1=Stop Motor and Alarm on I/O Fault; 0=Alarm only on I/O Fault	Time to echo back running / stopped feedback in Simulation (sec)	Time after Start to get Run Feedback before Fault (sec)	Time after Stop to drop Run Feedback before Fault (sec)	Time to pulse Out_Reset to clear motor fault	1=Fail To Start Alarm must be acknowledged	Motor Failed to Start Alarm	Motor Failed to Start Alarm	Motor Failed to Start Alarm	Motor Failed to Start Alarm	1=Fail To Start Alarm exists and will be checked	Motor Failed to Start Alarm	1=Reset required to clear Fail To Start Alarm	Fail To Start Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	Motor Failed to Start Alarm	1=Fail To Stop Alarm must be acknowledged	Motor Failed to Stop Alarm	Motor Failed to Stop Alarm	Motor Failed to Stop Alarm	Motor Failed to Stop Alarm	1=Fail To Stop Alarm exists and will be checked	Motor Failed to Stop Alarm	1=Reset required to clear Fail To Stop Alarm	Fail To Stop Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	Motor Failed to Stop Alarm	1=Acknowledge required for Interlock Trip Alarm	Interlock Trip Alarm	Interlock Trip Alarm	Interlock Trip Alarm	Interlock Trip Alarm	1=Interlock Tripped Alarm exists and will be checked	Interlock Trip Alarm	1=Reset required to clear Interlock Trip Alarm	Interlock Trip Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	Interlock Trip Alarm	1=Acknowledge required for I/O Fault Alarm	I/O Fault Alarm	I/O Fault Alarm	I/O Fault Alarm	I/O Fault Alarm	1=I/O Fault Alarm exists and will be checked	I/O Fault Alarm	1=Reset required to clear I/O Fault Alarm	I/O Fault Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	I/O Fault Alarm	1=Motor Fault Alarm must be acknowledged	Motor Faulted Alarm	Motor Faulted Alarm	Motor Faulted Alarm	Motor Faulted Alarm	Motor Faulted Alarm	Motor Faulted Alarm	1=Reset required to clear Motor Fault Alarm	Motor Fault Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	Motor Faulted Alarm	1=Operator (unlocked) exists, can be selected	1=Operator Locked exists, can be selected	1=Program (unlocked) exists, can be selected	1=Program Locked exists, can be selected	1=External exists, can be selected	1=Maintenance exists, can be selected	1=Maintenance Out of Service exists, can be selected	1=Override supersedes Prog/Oper Lock, 0=don't override Lock	1=External supersedes Prog/Oper Lock, 0=don't override Lock	1=Power Up to Prog, 0=Power Up to Oper	Normal Source: 1=Program if no requests; 0=Operator if no requests	Command Priority: 1=Program Cmds Win; 0=Operator Cmds Win	1=PCmd_Prog used as a Level (1=Prog, 0=Oper)	1=PCmd_Lock used as a Level (1=Lock, 0=Unlock)	1=XCmd_Acq used as Level (1=Acq, 0=Rel)
		Usage:		Local	Local	Local	Local	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local
		Data Type:		STRING_40	STRING_20	STRING_20	STRING_Area	BOOL	BOOL	BOOL	BOOL	BOOL	REAL	REAL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	REAL	REAL	REAL	REAL	BOOL	BOOL	BOOL	DINT	STRING_20	BOOL	DINT	BOOL	DINT	STRING_20	BOOL	BOOL	BOOL	DINT	STRING_20	BOOL	DINT	BOOL	DINT	STRING_20	BOOL	BOOL	BOOL	DINT	STRING_20	BOOL	DINT	BOOL	DINT	STRING_20	BOOL	BOOL	BOOL	DINT	STRING_20	BOOL	DINT	BOOL	DINT	STRING_20	BOOL	BOOL	BOOL	DINT	STRING_20	BOOL	DINT	BOOL	DINT	STRING_20	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL
			(Origin)	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.FailToStart.Cfg_	.FailToStart.Cfg_	.FailToStart.Cfg_	.FailToStart.Cfg_	.FailToStart.Cfg_	.FailToStart.Cfg_	.FailToStart.Cfg_	.FailToStart.Cfg_	.FailToStop.Cfg_	.FailToStop.Cfg_	.FailToStop.Cfg_	.FailToStop.Cfg_	.FailToStop.Cfg_	.FailToStop.Cfg_	.FailToStop.Cfg_	.FailToStop.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.MotorFault.Cfg_	.MotorFault.Cfg_	.MotorFault.Cfg_	.MotorFault.Cfg_	.MotorFault.Cfg_	.MotorFault.Cfg_	.MotorFault.Cfg_	.MotorFault.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_
Unit	Tag Description	TagName	Instance	Desc	Tag	Label	Area	HasJog	AllowLocal	HasPermObj	HasIntlkObj	HasMoreObj	MaxJogT	StartHornT	HasResInhObj	HasRunTimeObj	OperStopPrio	ExtStopPrio	OCmdResets	XCmdResets	OvrdPermIntlk	ShedOnFailToStart	ShedOnIOFault	SimFdbkT	FailToStartT	FailToStopT	ResetPulseT	AckReqd	AllowDisable	AllowShelve	AlmMinOnT	Cond	Exists	MaxShelfT	ResetReqd	Severity	Tag	AckReqd	AllowDisable	AllowShelve	AlmMinOnT	Cond	Exists	MaxShelfT	ResetReqd	Severity	Tag	AckReqd	AllowDisable	AllowShelve	AlmMinOnT	Cond	Exists	MaxShelfT	ResetReqd	Severity	Tag	AckReqd	AllowDisable	AllowShelve	AlmMinOnT	Cond	Exists	MaxShelfT	ResetReqd	Severity	Tag	AckReqd	AllowDisable	AllowShelve	AlmMinOnT	Cond	Exists	MaxShelfT	ResetReqd	Severity	Tag	HasOper	HasOperLocked	HasProg	HasProgLocked	HasExt	HasMaint	HasMOoS	OvrdOverLock	ExtOverLock	ProgPwrUp	ProgNormal	PCmdPriority	PCmdProgAsLevel	PCmdLockAsLevel	ExtAcqAsLevel
		Default Values:	0	SMC-50 Smart Motor Controller	P_SMC50	Motor Control	area01	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	10	15	15	2	1	1	1	5	Failed to Start	0	0	0	1000	XAR-nnnn	1	1	1	5	Failed to Stop	0	0	0	1000	XAS-nnnnA	1	1	1	5	Interlock Trip	0	0	0	500	XAS-nnnnB	1	1	1	5	I/O Fault	0	0	0	1000	XAF-nnnnB	1	1	1	5	Drive Fault	0	0	0	1000	XAF-nnnnA	1	1	1	1	0	1	1	1	0	0	0	0	0	0	0
		MyP_SMC50	1	SMC-Flex Smart Motor Controller	P_SMC50	Motor Control	area01	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	10	15	15	2	1	1	1	5	Failed to Start	0	0	0	4	XAR-nnnn	1	1	1	5	Failed to Stop	0	0	0	4	XAS-nnnnA	1	1	1	5	Interlock Trip	0	0	0	1	XAS-nnnnB	1	1	1	5	I/O Fault	0	0	0	4	XAF-nnnnB	1	1	1	5	Motor Fault	0	0	0	4	XAF-nnnnA	1	1	1	1	0	1	1	1	0	0	0	0	0	0	0
			2
			3
			4
			5
			6
			7
			8
			9
			10
			11
			12
			13
			14
			15
			16
			17
			18
			19
			20
			21
			22
			23
			24
			25
			26
			27
			28
			29
			30
			31
			32
			33
			34
			35
			36
			37
			38
			39
			40
			41
			42
			43
			44
			45
			46
			47
			48
			49
			50
			51
			52
			53
			54
			55
			56
			57
			58
			59
			60
			61
			62
			63
			64
			65
			66
			67
			68
			69
			70
			71
			72
			73
			74
			75
			76
			77
			78
			79
			80
			81
			82
			83
			84
			85
			86
			87
			88
			89
			90

## P_SMCFlex
	P_SMCFlex: SMC-Flex Smart Motor Controller	Read From CLX:
		Send To CLX:

		Description:		Description for display on HMI	Tagname for display on HMI	Label for graphic symbol displayed on HMI	Process Area for security	1=Power is in Megawatts (MW), 0=Power is in Kilowatts (kW)	1=Allow Local Start/Stop without alarm, 0=Start/Stop from HMI/prog only	1=Tells HMI a P_Perm is connected to Inp_Perm...	1=Tells HMI a P_Intlk is connected to Inp_Intlk	1=Tells HMI an object with more info is available	Maximum jog time (sec, 0=unlimited)	Time to sound audible on commanded start (sec) (0=disabled)	1=Tells HMI a P_ResInh Restart Inhibit is connected	1=Tells HMI a P_RunTime is connected	1=OCmd_Stop has priority, accepted any time, 0=OCmd_Stop only in Oper, Maint Mode.	1=XCmd_St0 any time, 0=XCmd_St0 only when Ext selected	1=New motor OCmd resets shed latches and cleared alarms, 0=OCmdReset reqd	1=New motor XCmd resets shed latches and cleared alarms, 0=XCmdReset reqd	1=Override ignores Bypassable Perm/ Intlk; 0=always use Perm/Intlk	1=Stop Motor and Alarm on Fail to Start; 0=Alarm only on Fail to Start	1=Stop Motor and Alarm on I/O Fault; 0=Alarm only on I/O Fault	Time to echo back running / stopped feedback in Simulation (sec)	Time after Start to get Run Feedback before Fault (sec)	Time after Stop to drop Run Feedback before Fault (sec)	Time to pulse Out_Reset to clear motor fault	Motor Failed to Start Alarm	Motor Failed to Start Alarm	Motor Failed to Start Alarm	Motor Failed to Start Alarm	Motor Failed to Start Alarm	1=Fail To Start Alarm exists and will be checked	Motor Failed to Start Alarm	1=Reset required to clear Fail To Start Alarm	Fail To Start Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	Motor Failed to Start Alarm	1=Fail To Stop Alarm must be acknowledged	Motor Failed to Stop Alarm	Motor Failed to Stop Alarm	Motor Failed to Stop Alarm	Motor Failed to Stop Alarm	1=Fail To Stop Alarm exists and will be checked	Motor Failed to Stop Alarm	1=Reset required to clear Fail To Stop Alarm	Fail To Stop Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	Motor Failed to Stop Alarm	1=Acknowledge required for Interlock Trip Alarm	Interlock Trip Alarm	Interlock Trip Alarm	Interlock Trip Alarm	Interlock Trip Alarm	1=Interlock Tripped Alarm exists and will be checked	Interlock Trip Alarm	1=Reset required to clear Interlock Trip Alarm	Interlock Trip Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	Interlock Trip Alarm	1=Acknowledge required for I/O Fault Alarm	I/O Fault Alarm	I/O Fault Alarm	I/O Fault Alarm	I/O Fault Alarm	1=I/O Fault Alarm exists and will be checked	I/O Fault Alarm	1=Reset required to clear I/O Fault Alarm	I/O Fault Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	I/O Fault Alarm	1=Motor Fault Alarm must be acknowledged	Motor Faulted Alarm	Motor Faulted Alarm	Motor Faulted Alarm	Motor Faulted Alarm	Motor Faulted Alarm	Motor Faulted Alarm	1=Reset required to clear Motor Fault Alarm	Motor Fault Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	Motor Faulted Alarm	1=Operator (unlocked) exists, can be selected	1=Operator Locked exists, can be selected	1=Program (unlocked) exists, can be selected	1=Program Locked exists, can be selected	1=External exists, can be selected	1=Maintenance exists, can be selected	1=Maintenance Out of Service exists, can be selected	1=Override supersedes Prog/Oper Lock, 0=don't override Lock	1=External supersedes Prog/Oper Lock, 0=don't override Lock	1=Power Up to Prog, 0=Power Up to Oper	Normal Source: 1=Program if no requests; 0=Operator if no requests	Command Priority: 1=Program Cmds Win; 0=Operator Cmds Win	1=PCmd_Prog used as a Level (1=Prog, 0=Oper)	1=PCmd_Lock used as a Level (1=Lock, 0=Unlock)	1=XCmd_Acq used as Level (1=Acq, 0=Rel)
		Usage:		Local	Local	Local	Local	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local
		Data Type:		STRING_40	STRING_20	STRING_20	STRING_Area	BOOL	BOOL	BOOL	BOOL	BOOL	REAL	REAL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	REAL	REAL	REAL	REAL	BOOL	BOOL	BOOL	DINT	STRING_20	BOOL	DINT	BOOL	DINT	STRING_20	BOOL	BOOL	BOOL	DINT	STRING_20	BOOL	DINT	BOOL	DINT	STRING_20	BOOL	BOOL	BOOL	DINT	STRING_20	BOOL	DINT	BOOL	DINT	STRING_20	BOOL	BOOL	BOOL	DINT	STRING_20	BOOL	DINT	BOOL	DINT	STRING_20	BOOL	BOOL	BOOL	DINT	STRING_20	BOOL	DINT	BOOL	DINT	STRING_20	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL
			(Origin)	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.FailToStart.Cfg_	.FailToStart.Cfg_	.FailToStart.Cfg_	.FailToStart.Cfg_	.FailToStart.Cfg_	.FailToStart.Cfg_	.FailToStart.Cfg_	.FailToStart.Cfg_	.FailToStop.Cfg_	.FailToStop.Cfg_	.FailToStop.Cfg_	.FailToStop.Cfg_	.FailToStop.Cfg_	.FailToStop.Cfg_	.FailToStop.Cfg_	.FailToStop.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.MotorFault.Cfg_	.MotorFault.Cfg_	.MotorFault.Cfg_	.MotorFault.Cfg_	.MotorFault.Cfg_	.MotorFault.Cfg_	.MotorFault.Cfg_	.MotorFault.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_
Unit	Tag Description	TagName	Instance	Desc	Tag	Label	Area	PwrUnits	AllowLocal	HasPermObj	HasIntlkObj	HasMoreObj	MaxJogT	StartHornT	HasResInhObj	HasRunTimeObj	OperStopPrio	ExtStopPrio	OCmdResets	XCmdResets	OvrdPermIntlk	ShedOnFailToStart	ShedOnIOFault	SimFdbkT	FailToStartT	FailToStopT	ResetPulseT	AckReqd	AllowDisable	AllowShelve	AlmMinOnT	Cond	Exists	MaxShelfT	ResetReqd	Severity	Tag	AckReqd	AllowDisable	AllowShelve	AlmMinOnT	Cond	Exists	MaxShelfT	ResetReqd	Severity	Tag	AckReqd	AllowDisable	AllowShelve	AlmMinOnT	Cond	Exists	MaxShelfT	ResetReqd	Severity	Tag	AckReqd	AllowDisable	AllowShelve	AlmMinOnT	Cond	Exists	MaxShelfT	ResetReqd	Severity	Tag	AckReqd	AllowDisable	AllowShelve	AlmMinOnT	Cond	Exists	MaxShelfT	ResetReqd	Severity	Tag	HasOper	HasOperLocked	HasProg	HasProgLocked	HasExt	HasMaint	HasMOoS	OvrdOverLock	ExtOverLock	ProgPwrUp	ProgNormal	PCmdPriority	PCmdProgAsLevel	PCmdLockAsLevel	ExtAcqAsLevel
		Default Values:	0	SMC-Flex Smart Motor Controller	P_SMCFlex	Motor Control	area01	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	10	15	15	2	1	1	1	5	Failed to Start	0	0	0	1000	XAR-nnnn	1	1	1	5	Failed to Stop	0	0	0	1000	XAS-nnnnA	1	1	1	5	Interlock Trip	0	0	0	500	XAS-nnnnB	1	1	1	5	I/O Fault	0	0	0	1000	XAF-nnnnB	1	1	1	5	Drive Fault	0	0	0	1000	XAF-nnnnA	1	1	1	1	0	1	1	1	0	0	0	0	0	0	0
		MyP_SMCFlex	1	SMC-Flex Smart Motor Controller	HC101	Motor Soft Starter	area01	0	0	0	0	0	0	0	0	0	0	0	0	0	10	15	15	2	1	1	1	5	Failed to Start	0	480	0	4	XAR-nnnn	1	1	1	5	Failed to Stop	0	480	0	4	XAS-nnnnA	1	1	1	5	Interlock Trip	0	480	0	1	XAS-nnnnB	1	1	1	5	I/O Fault	0	480	0	4	XAF-nnnnB	1	1	1	5	Motor Fault	0	480	0	4	XAF-nnnnA	1	1	1	1	0	1	1	1	0	0	0	0	0	0	0
			2
			3
			4
			5
			6
			7
			8
			9
			10
			11
			12
			13
			14
			15
			16
			17
			18
			19
			20
			21
			22
			23
			24
			25
			26
			27
			28
			29
			30
			31
			32
			33
			34
			35
			36
			37
			38
			39
			40
			41
			42
			43
			44
			45
			46
			47
			48
			49
			50
			51
			52
			53
			54
			55
			56
			57
			58
			59
			60
			61
			62
			63
			64
			65
			66
			67
			68
			69
			70
			71
			72
			73
			74
			75
			76
			77
			78
			79
			80
			81
			82
			83
			84
			85
			86
			87
			88
			89
			90

## P_StrapTbl
	P_StrapTbl: Tank Strapping Table	Read From CLX:
		Send To CLX:

		Description:		Description for display on HMI	Label for graphic symbol displayed on HMI	Tagname for display on HMI	Process Area for security	Level Engineering Units for display on HMI	Temperature Engineering Units for display on HMI	Volume Engineering Units for display on HMI	Table Minor Units (in, cm, mm) per Major Unit (ft, m) (enter 0.0 if minor units not used)	1=Include Correction for Temperature of tank Shell, 0=No CTSh	1=Include Floating Roof Adjustment, 0=no FRA	Temperature of Tank Calibration (typ. 60 Deg F or 15 Deg C)	Tank Shell Linear Coefficient of Thermal Expansion (feet/Deg F or meters/Deg C)	Temp. weighting (enter 0.0 for insulated tank) (see API MPMS 2.2A app. D)	Lowest level at which to add/sub floating roof comp. (feet)	Degrees API for which table includes floating roof data	Adjustment to table values for API <> CalAPI (vol/deg API, typ. a neg. #)	1=Tells HMI an object with more info is available
		Usage:		Local	Local	Local	Local	Local	Local	Local	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input
		Data Type:		STRING_40	STRING_20	STRING_20	STRING_Area	STRING_8	STRING_8	STRING_8	REAL	BOOL	BOOL	REAL	REAL	REAL	REAL	REAL	REAL	BOOL
			(Origin)	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_
Unit	Tag Description	TagName	Instance	Desc	Label	Tag	Area	LevelEU	TempEU	VolumeEU	MinorPerMajor	HasCTSh	HasFRA	CalTemp	ShellCoefOfExp	K	FloatRoofLevel	FloatRoofCalAPI	FloatRoofVolPerAPI	HasMoreObj
		Default Values:	0	Tank Strapping Table	Stripping Table	P_StrapTbl	area01	Feet	Deg F	Gallons	12.0	0	0	60.0	0.0000062	7.0	0.0	30.5	-2.5	0
		MyP_StrapTbl	1	Tank Strapping Table	Strapping Table	P_StrapTbl	area01	Feet	Deg F	Gallons	12	0	0	60	6.1999999161344E-06	7	0	30.5	-2.5	0
			2
			3
			4
			5
			6
			7
			8
			9
			10
			11
			12
			13
			14
			15
			16
			17
			18
			19
			20
			21
			22
			23
			24
			25
			26
			27
			28
			29
	NOTE:		30	Strings too long to fit are formatted like this
	Tank Calibration Table Values (Major Level		31
	Units, Minor Level Units and corresponding		32
	Volume at each calibration point) are stored		33
	in a separate Tag. Use the Tank Calibration		34
	Table Sheet "P_StrapTblCfg" (or copies of		35
	it) to read / save / restore these values.		36
			37
			38
			39
			40
			41
			42
			43
			44
			45
			46
			47
			48
			49
			50
			51
			52
			53
			54
			55
			56
			57
			58
			59
			60
			61
			62
			63
			64
			65
			66
			67
			68
			69
			70
			71
			72
			73
			74
			75
			76
			77
			78
			79
			80
			81
			82
			83
			84
			85
			86
			87
			88
			89
			90
			91
			92
			93
			94
			95
			96
			97
			98
			99

## P_ValveC
	P_ValveC: Control Valve	Read From CLX:
		Send To CLX:

		Description:		Description for display on HMI	Label for graphic symbol displayed on HMI	Tagname for display on HMI	Process Area for security	Engineering Units for display on HMI	CV Minimum in Engineering Units (for scaling)	CV Maximum in Engineering Units (for scaling)	CV Minimum in I/O (raw) Units (for scaling)	CV Maximum in I/O (raw) Units (for scaling)	Number of decimal places for CV display (0..6)	Position Feedback Minimum in raw input units (for scaling)	Position Feedback Maximum in raw input units (for scaling)	Minimum CV (in CV EU, for limiting)	Maximum CV (in CV EU, for limiting)	CV Rate of Change Limit, Increasing, (EU/sec, 0=unlimited)	CV Rate of Change Limit, Decreasing, (EU/sec, 0=unlimited)	1=Value provides an analog position feedback, 0=simulate feedback	1=Clamps Val_Pos to EUMin/Max when on a Limit Switch	1=Skip RoC Limiting in Intlk, Maint, Ovrd modes	Open and Close Pulse Output overall period (s)	Rate at which valve moves when opening (CV EU/sec)	Rate at which valve moves when closing (CV EU/sec)	Open and Close Pulse Output maximum ON time (s)	Open and Close Pulse Output minimum ON time (s)	Time to bump valve open or closed (by Oper) when Fdbk Bad (sec)	Additional time on first pulse after stop or direction change	Position above which valve is assumed open if limit switches not used	1=Valve provides an Open Limit Switch signal	1=Valve provides a Closed Limit Switch signal	1=Valve Open LS should be used for open/closed status	1=Valve Closed LS should be used for open/closed status	1=both switches ON=fail, 0=both switches OFF=fail	1=Hold Output on Interlock or bad PV, 0=Go to Cfg_IntlkCV	1=Take shed action (hold or interlock CV) on I/O Fault	CV (target in EU) when interlocked (if not Cfg_ShedHold)	1=Tells HMI a P_Intlk is connected to Inp_Intlk	1=Tells HMI an object with more info is available	1=Tells HMI to enable navigation to a connected CV object	Tagname for destination of CV Navigation button	Interlock Tripped Alarm Condition	Interlock Tripped Alarm Tag	1=Interlock Tripped Alarm exists and will be checked	1=Reset required to clear Interlock Trip Alarm	1=Acknowledge required for Interlock Trip Alarm	Interlock Trip Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	Actuator Fault Alarm Condition	Actuator Fault Alarm Tag	1=Actuator Fault Alarm exists and will be checked	1=Reset required to clear Actuator Fault Alarm	1=Acknowledge required for Actuator Fault Alarm	Actuator Fault Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	I/O Fault Alarm Condition	I/O Fault Alarm Tag	1=I/O Fault Alarm exists and will be checked	1=Reset required to clear I/O Fault Alarm	1=Acknowledge required for I/O Fault Alarm	I/O Fault Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	1=PSets track OSets in Oper, OSets track PSets in Prog, 0=no tracking	1=Prog/Oper Settings track Override/Hand CV	1=Override ignores Bypassable Intlk; 0=always use Intlk	1=Operator (unlocked) exists, can be selected	1=Operator Locked exists, can be selected	1=Program (unlocked) exists, can be selected	1=Program Locked exists, can be selected	1=External exists, can be selected	1=Maintenance exists, can be selected	1=Maintenance Out of Service exists, can be selected	1=Override supersedes Prog/Oper Lock, 0=don't override Lock	1=External supersedes Prog/Oper Lock, 0=don't override Lock	1=Power Up to Prog, 0=Power Up to Oper	Normal Source: 1=Program if no requests; 0=Operator if no requests	Command Priority: 1=Program Cmds Win; 0=Operator Cmds Win	1=PCmd_Prog used as a Level (1=Prog, 0=Oper)	1=PCmd_Lock used as a Level (1=Lock, 0=Unlock)	1=XCmd_Acq used as Level (1=Acq, 0=Rel)
		Usage:		Local	Local	Local	Local	Local	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Input	Input	Input	Local	Local	Local	Local	Local	Local	Local	Local
		Data Type:		STRING_40	STRING_20	STRING_20	STRING_Area	STRING_8	REAL	REAL	REAL	REAL	DINT	REAL	REAL	REAL	REAL	REAL	REAL	BOOL	BOOL	BOOL	REAL	REAL	REAL	REAL	REAL	REAL	REAL	REAL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	REAL	BOOL	BOOL	BOOL	STRING_NavTag	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL
			(Origin)	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.ActuatorFault.Cfg_	.ActuatorFault.Cfg_	.ActuatorFault.Cfg_	.ActuatorFault.Cfg_	.ActuatorFault.Cfg_	.ActuatorFault.Cfg_	.ActuatorFault.Cfg_	.ActuatorFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.Cfg_	.Cfg_	.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_
Unit	Tag Description	TagName	Instance	Desc	Label	Tag	Area	EU	CVEUMin	CVEUMax	CVRawMin	CVRawMax	DecPlcs	FdbkRawMin	FdbkRawMax	MinCV	MaxCV	CVRoCLimInc	CVRoCLimDec	HasPosFdbk	ClampPosToLS	SkipRoCLim	CycleT	OpenRate	CloseRate	MaxOnT	MinOnT	BumpT	Deadtime	MaxClosedPos	HasOpenLS	HasClosedLS	UseOpenLS	UseClosedLS	LSFail	ShedHold	ShedOnIOFault	IntlkCV	HasIntlkObj	HasMoreObj	HasCVNav	CVNavTag	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	SetTrack	SetTrackOvrdHand	OvrdIntlk	HasOper	HasOperLocked	HasProg	HasProgLocked	HasExt	HasMaint	HasMOoS	OvrdOverLock	ExtOverLock	ProgPwrUp	ProgNormal	PCmdPriority	PCmdProgAsLevel	PCmdLockAsLevel	ExtAcqAsLevel
		Default Values:	0	Analog Output	Analog Output	P_AOut	area01	%	0.0	100.0	0.0	100.0	0	0.0	100.0	0.0	100.0	0	0	1	1	0	10.0	1.0	1.0	5	1	0.0	0.0	0.0	0	0	0	0	1	0	0	0.0	0	0	0		Interlock Trip	P_ValveC.IntlkTrip	0	0	1	500	0	1	5	480	Actuator Fault	P_ValveC.ActFault	0	0	1	1000	0	1	5	480	I/O Fault	P_ValveC.IOFault	0	0	1	1000	0	1	5	480	1	0	0	1	1	1	1	0	1	1	1	0	0	0	0	0	0	0
		MyP_ValveC	1	Pulse Output Valve	Analog Valve	MyValveC	area01	% Open	0	100	0	100	0	0	100	0	100	0	0	1	1	0	10	0.400000005960465	0.400000005960465	10	2	2	0	1	1	1	1	1	1	0	0	0	0	0	0		Interlock Trip	MyValveC.IntlkTrip	1	0	1	3	1	1	5	480	Actuator Fault	MyValveC.ActFault	1	0	1	3	1	1	5	480	I/O Fault	MyValveC.IOFault	1	0	1	3	1	1	5	480	1	0	0	1	1	1	1	0	1	1	1	0	0	0	0	0	0	0
			2
			3
			4
			5
			6
			7
			8
			9
			10
			11
			12
			13
			14
			15
			16
			17
			18
			19
			20
			21
			22
			23
			24
			25
			26
			27
			28
			29
			30	Strings too long to fit are formatted like this
			31
			32
			33
			34
			35
			36
			37
			38
			39
			40
			41
			42
			43
			44
			45
			46
			47
			48
			49
			50
			51
			52
			53
			54
			55
			56
			57
			58
			59
			60
			61
			62
			63
			64
			65
			66
			67
			68
			69
			70
			71
			72
			73
			74
			75
			76
			77
			78
			79
			80
			81
			82
			83
			84
			85
			86
			87
			88
			89
			90
			91
			92
			93
			94
			95
			96
			97
			98
			99

## P_ValveHO
	P_ValveHO: Hand Operated Valve	Read From CLX:
		Send To CLX:

		Description:		Description for display on HMI	Label for graphic symbol displayed on HMI	Tagname for display on HMI	Process Area for security	1=Valve provides an Open Limit Switch signal	1=Valve provides a Closed Limit Switch signal	1=Valve Open LS should be used for failure checking	1=Valve Closed LS should be used for failure checking	1=both switches ON=fail, 0=both switches OFF=fail	1=Trip Output is connected to valve, 0=Monitor only	1=Trip opens valve, 0=Trip closes valve	After tripped, time to reach trip position before Alarm (sec)	1=Continue Trip and Alarm on Fail to Trip; 0=Alarm only on Fail to Trip	1=Trip Motor and Alarm on I/O Fault; 0=Alarm only on I/O Fault	1=New Oper trip cmd. resets fault, 0=reset reqd to clear fault	Delay to echo back of Open/Closed status when in Simulation (sec)	1=Tells HMI a P_Intlk is connected to Inp_Intlk	1=Tells HMI a P_ValveStats is monitoring this valve	1=Tells HMI an object with more info is available	Time not confirmed open or closed before Alarm (sec)	Fail to Trip Alarm Condition	Fail to Trip Alarm Tag	1=Fail to Trip Alarm exists and will be checked	1=Reset required to clear Fail to Trip Alarm	1=Fail to Trip Alarm must be acknowledged	Fail to Trip Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	Transit Stall Alarm Condition	Transit Stall Alarm Tag	1=Transit Stall Alarm exists and will be checked	1=Reset required to clear Transit Stall Alarm	1=Acknowledge required for Transit Stall Alarm	Transit Stall Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	Interlock Tripped Alarm Condition	Interlock Tripped Alarm Tag	1=Interlock Tripped Alarm exists and will be checked	1=Reset required to clear Interlock Trip Alarm	1=Acknowledge required for Interlock Trip Alarm	Interlock Trip Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	I/O Fault Alarm Condition	I/O Fault Alarm Tag	1=I/O Fault Alarm exists and will be checked	1=Reset required to clear I/O Fault Alarm	1=Acknowledge required for I/O Fault Alarm	I/O Fault Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)
		Usage:		Local	Local	Local	Local	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local
		Data Type:		STRING_40	STRING_20	STRING_20	STRING_Area	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	REAL	BOOL	BOOL	BOOL	REAL	BOOL	BOOL	BOOL	REAL	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT
			(Origin)	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.TripFail.Cfg_	.TripFail.Cfg_	.TripFail.Cfg_	.TripFail.Cfg_	.TripFail.Cfg_	.TripFail.Cfg_	.TripFail.Cfg_	.TripFail.Cfg_	.TransitStall.Cfg_	.TransitStall.Cfg_	.TransitStall.Cfg_	.TransitStall.Cfg_	.TransitStall.Cfg_	.TransitStall.Cfg_	.TransitStall.Cfg_	.TransitStall.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_
Unit	Tag Description	TagName	Instance	Desc	Label	Tag	Area	HasOpenLS	HasClosedLS	UseOpenLS	UseClosedLS	LSFail	HasTrip	TripOpen	TripFailT	ShedOnFailToTrip	ShedOnIOFault	OCmdResets	SimFdbkT	HasIntlkObj	HasStatsObj	HasMoreObj	TransitStallT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT
		Default Values:	0	Hand Operated Valve	Valve Monitor	P_ValveHO	area01	1	1	1	1	1	0	0	10	1	1	0	3	0	0	0	60	Failed to Trip	P_ValveHO.FailToTrip	0	0	1	1000	0	1	5	480	Transit Stall	P_ValveHO.TransStall	0	0	1	1000	0	1	5	480	Interlock Trip	P_ValveHO.IntlkTrip	0	0	1	500	0	1	5	480	I/O Fault	P_ValveHO.IOFault	0	0	1	1000	0	1	5	480
		MyP_ValveHO	1	Station Inlet Valve (Hand Oper)	Station Inlet	MyValveHO	area01	0	1	0	1	1	1	0	5	1	1	0	2	1	0	0	20	Failed to Trip	MyValveHO.FailToTrip	1	0	1	3	1	1	5	480	Valve Transit Stall	Alarm Tag 1234567890	0	0	1	3	1	1	5	0	Interlock Trip	MyValveHO.IntlkTrip	1	0	1	3	1	1	5	480	I/O Fault	MyValveHO.IOFault	1	0	1	3	1	1	5	480
			2
			3
			4
			5
			6
			7
			8
			9
			10
			11
			12
			13
			14
			15
			16
			17
			18
			19
			20
			21
			22
			23
			24
			25
			26
			27
			28
			29
			30	Strings too long to fit are formatted like this
			31
			32
			33
			34
			35
			36
			37
			38
			39
			40
			41
			42
			43
			44
			45
			46
			47
			48
			49
			50
			51
			52
			53
			54
			55
			56
			57
			58
			59
			60
			61
			62
			63
			64
			65
			66
			67
			68
			69
			70
			71
			72
			73
			74
			75
			76
			77
			78
			79
			80
			81
			82
			83
			84
			85
			86
			87
			88
			89
			90
			91
			92
			93
			94
			95
			96
			97
			98
			99

## P_ValveMO
	P_ValveMO: Motor Operated Valve	Read From CLX:
		Send To CLX:

		Description:		Description for display on HMI	Label for graphic symbol displayed on HMI	Tagname for display on HMI	Process Area for security	1=Stop output can be used to break local seal-in and stop valve motion	Time (in seconds) to pulse valve outputs (0 = outputs maintained ON)	1=Valve provides an Open Limit Switch signal	1=Valve provides a Closed Limit Switch signal	1=Valve Open LS should be used for failure checking	1=Valve Closed LS should be used for failure checking	1=Coasting into LS when stoped changes state (compact. With 3.5-04), 0= Stop is independent	1=both switches ON=fail, 0=both switches OFF=fail	After command, time with no motion before Fault (sec)	After command, time to reach position before Fault (sec)	Time to sound audible on commanded energize (sec) (0=disabled)	1=Stop Valve and Alarm on Full Stall; 0=Alarm only on Full Stall	1=Stop Valve and Alarm on Transit Stall; 0=Alarm only on Transit Stall	1=Stop Valve and Alarm on Actuator Fault; 0=Alarm only on Actuator Fault	1=Stop Valve and Alarm on I/O Fault; 0=Alarm only on I/O Fault	Delay to echo back of Open/Closed status when in Simulation (sec)	1=Tells HMI a P_Perm connected to Inp_OpenPermOK	1=Tells HMI a P_Perm connected to Inp_ClosePermOK	1=Tells HMI a P_ValveStats is monitoring this valve	1=Tells HMI an object with more info is available	Full Stall Alarm Condition	Full Stall Alarm Tag	1=Full Stall Alarm exists and will be checked	1=Reset required to clear Full Stall Alarm	1=Acknowledge required for Full Stall Alarm	Full Stall Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	Transit Stall Alarm Condition	Transit Stall Alarm Tag	1=Transit Stall Alarm exists and will be checked	1=Reset required to clear Transit Stall Alarm	1=Acknowledge required for Transit Stall Alarm	Transit Stall Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	Actuator Fault Alarm Condition	Actuator Fault Alarm Tag	1=Actuator Fault Alarm exists and will be checked	1=Reset required to clear Actuator Fault Alarm	1=Acknowledge required for Actuator Fault Alarm	Actuator Fault Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	I/O Fault Alarm Condition	I/O Fault Alarm Tag	1=I/O Fault Alarm exists and will be checked	1=Reset required to clear I/O Fault Alarm	1=Acknowledge required for I/O Fault Alarm	I/O Fault Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	1=New Oper valve cmd. resets fault, 0=reset reqd to clear fault	1=New Valve XCmd resets shed latches and cleared alarms, 0=XCmdReset reqd	1=Override ignores Bypassable Perms; 0=always use Perms	1=Operator (unlocked) exists, can be selected	1=Operator Locked exists, can be selected	1=Program (unlocked) exists, can be selected	1=Program Locked exists, can be selected	1=External exists, can be selected	1=Maintenance exists, can be selected	1=Maintenance Out of Service exists, can be selected	1=Override supersedes Prog/Oper Lock, 0=don't override Lock	1=External supersedes Prog/Oper Lock, 0=don't override Lock	1=Power Up to Prog, 0=Power Up to Oper	Normal Source: 1=Program if no requests; 0=Operator if no requests	Command Priority: 1=Program Cmds Win; 0=Operator Cmds Win	1=PCmd_Prog used as a Level (1=Prog, 0=Oper)	1=PCmd_Lock used as a Level (1=Lock, 0=Unlock)	1=XCmd_Acq used as Level (1=Acq, 0=Rel)
		Usage:		Local	Local	Local	Local	Input	Input	Input	Input	Input	Input		Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Input	Input	Input	Local	Local	Local	Local	Local	Local	Local	Local
		Data Type:		STRING_40	STRING_20	STRING_20	STRING_Area	BOOL	REAL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	REAL	REAL	REAL	BOOL	BOOL	BOOL	BOOL	REAL	BOOL	BOOL	BOOL	BOOL	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL
			(Origin)	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.FullStall.Cfg_	.FullStall.Cfg_	.FullStall.Cfg_	.FullStall.Cfg_	.FullStall.Cfg_	.FullStall.Cfg_	.FullStall.Cfg_	.FullStall.Cfg_	.TransitStall.Cfg_	.TransitStall.Cfg_	.TransitStall.Cfg_	.TransitStall.Cfg_	.TransitStall.Cfg_	.TransitStall.Cfg_	.TransitStall.Cfg_	.TransitStall.Cfg_	.ActuatorFault.Cfg_	.ActuatorFault.Cfg_	.ActuatorFault.Cfg_	.ActuatorFault.Cfg_	.ActuatorFault.Cfg_	.ActuatorFault.Cfg_	.ActuatorFault.Cfg_	.ActuatorFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.Cfg_	.Cfg_	.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_
Unit	Tag Description	TagName	Instance	Desc	Label	Tag	Area	HasStop	OutPulseT	HasOpenLS	HasClosedLS	UseOpenLS	UseClosedLS	CoastTolS	LSFail	FullStallT	TransitStallT	StartHornT	ShedOnFullStall	ShedOnTransitStall	ShedOnActuatorFault	ShedOnIOFault	SimFdbkT	HasOpenPermObj	HasClosePermObj	HasStatsObj	HasMoreObj	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	OCmdResets	XCmdResets	OvrdPerm	HasOper	HasOperLocked	HasProg	HasProgLocked	HasExt	HasMaint	HasMOoS	OvrdOverLock	ExtOverLock	ProgPwrUp	ProgNormal	PCmdPriority	PCmdProgAsLevel	PCmdLockAsLevel	ExtAcqAsLevel
		Default Values:	0	Motor Operated Valve	Valve Control	P_ValveMO	area01	0	5	0	0	0	0	1	1	15	60	0	1	1	1	1	20	0	0	0	0	Full Stall	P_ValveMO.FullStall	0	0	1	1000	0	1	5	480	Transit Stall	P_ValveMO.TransStall	0	0	1	1000	0	1	5	480	Actuator Fault	P_ValveMO.ActFault	0	0	1	1000	0	1	5	480	I/O Fault	P_ValveMO.IOFault	0	0	1	1000	0	1	5	480	0	0	0	1	1	1	1	0	1	1	1	0	0	0	0	0	0	0
		MyP_ValveMO	1	Motor Operated Valve	Valve Control	MyValveMO	area01	1	5	0	0	0	0	1	1	15	60	0	1	1	1	1	5	1	1	1	0	Valve Full Stall	MyValveMO.FullStall	0	0	1	3	1	1	5	480	Valve Transit Stall	MyValveMO.TransStall	0	0	1	3	1	1	5	480	Actuator Fault	MyValveMO.ActFault	1	0	1	3	1	1	5	480	I/O Fault	MyValveMO.IOFault	1	0	1	3	1	1	5	480	0	0	0	1	1	1	1	0	1	1	1	0	0	0	0	0	0	0
			2
			3
			4
			5
			6
			7
			8
			9
			10
			11
			12
			13
			14
			15
			16
			17
			18
			19
			20
			21
			22
			23
			24
			25
			26
			27
			28
			29
			30	Strings too long to fit are formatted like this
			31
			32
			33
			34
			35
			36
			37
			38
			39
			40
			41
			42
			43
			44
			45
			46
			47
			48
			49
			50
			51
			52
			53
			54
			55
			56
			57
			58
			59
			60
			61
			62
			63
			64
			65
			66
			67
			68
			69
			70
			71
			72
			73
			74
			75
			76
			77
			78
			79
			80
			81
			82
			83
			84
			85
			86
			87
			88
			89
			90
			91
			92
			93
			94
			95
			96
			97
			98
			99

## P_ValveMP
	P_ValveMP: Mix Proof Valve	Read From CLX:
		Send To CLX:

		Description:		Description for display on HMI	Label for graphic symbol displayed on HMI	Tagname for display on HMI	Process Area for security	1=Valve supports Lift Lower Seat state (4)	1=Valve supports Lift Upper Seat state (5)	1=Valve supports SIP Cavity state (6)	1=Valve supports SIP Lower Seat state (8)	1=Valve supports SIP Upper Seat state (10)	1=Pulse seat lift output when doing Lift Lower	1=Pulse seat lift output when doing Lift Upper	1=Pulse seat lift output when doing SIP/CIP Lower	1=Pulse seat lift output when doing SIP/CIP Upper	Time to lift seat when pulsing seat for cleaning (sec)	Time to close seat when pulsing seat for cleaning (sec)	Output States to drive valve to De-Energized State	Output States to drive valve to Closed State	Output States to drive valve to Cavity Out Closed State	Output States to drive valve to Opened State	Output States to drive valve to Lift Lower Seat State	Output States to drive valve to Lift Upper Seat State	Output States to drive valve to CIP/SIP Cavity State	Output States to drive valve to Lift Lower for CIP/SIP State	Output States to drive valve to CIP/SIP Lower Seat State	Output States to drive valve to Lift Upper for CIP/SIP State	Output States to drive valve to CIP/SIP Upper Seat State	Feedback Input states to achieve De-Energized State	Feedback Input states to achieve Closed State	Feedback Input states to achieve Cavity Out Closed State	Feedback Input states to achieve Opened State	Feedback Input states to achieve Lift Lower Seat State	Feedback Input states to achieve Lift Upper Seat State	Feedback Input states to achieve CIP/SIP Cavity State	Feedback Input states to achieve Lift Lower for CIP/SIP State	Feedback Input states to achieve CIP/SIP Lower Seat State	Feedback Input states to achieve Lift Upper for CIP/SIP State	Feedback Input states to achieve CIP/SIP Upper Seat State	Feedback Inputs checked to achieve De-Energized State	Feedback Inputs checked to achieve Closed State	Feedback Inputs checked to achieve Cavity Out Closed State	Feedback Inputs checked to achieve Opened State	Feedback Inputs checked to achieve Lift Lower Seat State	Feedback Inputs checked to achieve Lift Upper Seat State	Feedback Inputs checked to achieve CIP/SIP Cavity State	Feedback Inputs checked to achieve Lift Lower for CIP/SIP State	Feedback Inputs checked to achieve CIP/SIP Lower Seat State	Feedback Inputs checked to achieve Lift Upper for CIP/SIP State	Feedback Inputs checked to achieve CIP/SIP Upper Seat State	Feedback Match Time required to achieve De-Energized State	Feedback Match Time required to achieve Closed State	Feedback Match Time required to achieve Cavity Out Closed State	Feedback Match Time required to achieve Opened State	Feedback Match Time required to achieve Lift Lower Seat State	Feedback Match Time required to achieve Lift Upper Seat State	Feedback Match Time required to achieve CIP/SIP Cavity State	Feedback Match Time required to achieve Lift Lower for CIP/SIP State	Feedback Match Time required to achieve CIP/SIP Lower Seat State	Feedback Match Time required to achieve Lift Upper for CIP/SIP State	Feedback Match Time required to achieve CIP/SIP Upper Seat State	1=Close Valve and Alarm on Position Fail; 0=Alarm only on Fail	1=Close Valve and Alarm on I/O Fault; 0=Alarm only on I/O Fault	1=Tells HMI a P_Perm is connected to Inp_Perm	1=Tells HMI a P_Intlk is connected to Inp_Intlk	1=Tells HMI a P_ValveStats is monitoring this valve	1=Tells HMI an object with more info is available	Time to give valve to achieve state before declaring valve failure (sec)	Valve Failure Alarm Condition	Valve Failure Alarm Tag	1=Valve Failure Alarm exists and will be checked	1=Reset required to clear Valve Failure Alarm	1=Acknowledge required for Valve Failure Alarm	Valve Failure Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	Interlock Tripped Alarm Condition	Interlock Tripped Alarm Tag	1=Interlock Tripped Alarm exists and will be checked	1=Reset required to clear Interlock Trip Alarm	1=Acknowledge required for Interlock Trip Alarm	Interlock Trip Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	I/O Fault Alarm Condition	I/O Fault Alarm Tag	1=I/O Fault Alarm exists and will be checked	1=Reset required to clear I/O Fault Alarm	1=Acknowledge required for I/O Fault Alarm	I/O Fault Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	1=New Oper pos. cmd. resets fault, 0=reset reqd to clear fault	1=New Valve XCmd resets shed latches and cleared alarms, 0=XCmdReset reqd	1=Override ignores Bypassable Perm/ Intlk; 0=always use Perm/Intlk	1=Operator (unlocked) exists, can be selected	1=Operator Locked exists, can be selected	1=Program (unlocked) exists, can be selected	1=Program Locked exists, can be selected	1=External exists, can be selected	1=Maintenance exists, can be selected	1=Maintenance Out of Service exists, can be selected	1=Override supersedes Prog/Oper Lock, 0=don't override Lock	1=External supersedes Prog/Oper Lock, 0=don't override Lock	1=Power Up to Prog, 0=Power Up to Oper	Normal Source: 1=Program if no requests; 0=Operator if no requests	Command Priority: 1=Program Cmds Win; 0=Operator Cmds Win	1=PCmd_Prog used as a Level (1=Prog, 0=Oper)	1=PCmd_Lock used as a Level (1=Lock, 0=Unlock)	1=XCmd_Acq used as Level (1=Acq, 0=Rel)
		Usage:		Local	Local	Local	Local	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input					Input	Input	Input	Input	Input	Input	Input	Local	Local	Local	Local	Local	Local	Local	Local	Input	Input	Input	Local	Local	Local	Local	Local	Local	Local	Local
		Data Type:		STRING_40	STRING_20	STRING_20	STRING_Area	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	REAL	REAL	SINT	SINT	SINT	SINT	SINT	SINT	SINT	SINT	SINT	SINT	SINT	SINT	REAL	REAL	REAL	REAL	REAL	REAL	REAL	REAL	REAL	REAL	REAL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	REAL	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL
			(Origin)	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Fail.Cfg_	.Fail.Cfg_	.Fail.Cfg_	.Fail.Cfg_	.Fail.Cfg_	.Fail.Cfg_	.Fail.Cfg_	.Fail.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.Cfg_	.Cfg_	.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_
Unit	Tag Description	TagName	Instance	Desc	Label	Tag	Area	HasLiftLower	HasLiftUpper	HasSIPCavity	HasSIPLower	HasSIPUpper	PulseLiftLower	PulseLiftUpper	PulseSIPLower	PulseSIPUpper	PulseOpenT	PulseCloseT	OutStateTbl[0]	OutStateTbl[1]	OutStateTbl[2]	OutStateTbl[3]	OutStateTbl[4]	OutStateTbl[5]	OutStateTbl[6]	OutStateTbl[7]	OutStateTbl[8]	OutStateTbl[9]	OutStateTbl[10]	FdbkStateTbl[0]	FdbkStateTbl[1]	FdbkStateTbl[2]	FdbkStateTbl[3]	FdbkStateTbl[4]	FdbkStateTbl[5]	FdbkStateTbl[6]	FdbkStateTbl[7]	FdbkStateTbl[8]	FdbkStateTbl[9]	FdbkStateTbl[10]	FdbkReqdTbl[0]	FdbkReqdTbl[1]	FdbkReqdTbl[2]	FdbkReqdTbl[3]	FdbkReqdTbl[4]	FdbkReqdTbl[5]	FdbkReqdTbl[6]	FdbkReqdTbl[7]	FdbkReqdTbl[8]	FdbkReqdTbl[9]	FdbkReqdTbl[10]	FdbkTimeTbl[0]	FdbkTimeTbl[1]	FdbkTimeTbl[2]	FdbkTimeTbl[3]	FdbkTimeTbl[4]	FdbkTimeTbl[5]	FdbkTimeTbl[6]	FdbkTimeTbl[7]	FdbkTimeTbl[8]	FdbkTimeTbl[9]	FdbkTimeTbl[10]	ShedOnFail	ShedOnIOFault	HasPermObj	HasIntlkObj	HasStatsObj	HasMoreObj	FailT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	OCmdResets	XCmdResets	OvrdPermIntlk	HasOper	HasOperLocked	HasProg	HasProgLocked	HasExt	HasMaint	HasMOoS	OvrdOverLock	ExtOverLock	ProgPwrUp	ProgNormal	PCmdPriority	PCmdProgAsLevel	PCmdLockAsLevel	ExtAcqAsLevel
		Default Values:	0	Mix Proof Valve	Valve Control	P_ValveMP	area01	0	0	0	0	0	0	0	0	0	10.0	5.0	2#0000_0000	2#0000_0001	2#0010_0000	2#0010_0010	2#0000_0100	2#0000_1000	2#0001_0000	2#0001_0100	2#0011_0100	2#0001_1000	2#0011_1000	2#0000_0001	2#0000_0001	2#0010_0000	2#0010_0010	2#0000_0100	2#0000_1000	2#0001_0000	2#0001_0100	2#0011_0100	2#0001_1000	2#0011_1000	2#0000_0000	2#0000_0000	2#0000_0000	2#0000_0000	2#0000_0000	2#0000_0000	2#0000_0000	2#0000_0000	1.0	1.0	1.0	1.0	1.0	1.0	1.0	1.0	1.0	1.0	1.0	0	1	0	0	0	0	3	Valve Failure	P_ValveMP.Fail	0	0	1	1000	0	1	5	480	Interlock Trip	P_ValveMP.IntlkTrip	0	0	1	500	0	1	5	480	I/O Fault	P_ValveMP.IOFault	0	0	1	1000	0	1	5	480	0	0	0	1	1	1	1	0	1	1	1	0	0	0	0	0	0	0
		MyP_ValveMP	1	Mix Proof Valve	Valve Control	TestValveMP	area01	1	1	1	1	1	0	0	1	1	10	5	0	1	32	34	4	8	16	20	52	24	56	1	1	32	2	4	8	16	20	52	24	56	0	0	0	0	0	0	0	0	0	0	0	1	1	1	1	1	1	1	1	1	1	1	1	1	0	0	0	0	5	Valve Failure	TestValveMP.Fail	0	0	1	3	1	1	5	480	Interlock Trip	TestValveMP.IntlkTri	1	0	1	3	1	1	5	480	I/O Fault	TestValveMP.IOFault	1	0	1	3	1	1	5	480	0	0	0	1	1	1	1	0	1	1	1	0	0	0	0	0	0	0
			2
			3
			4
			5
			6
			7
			8
			9
			10
			11
			12
			13
			14
			15
			16
			17
			18
			19
			20
			21
			22
			23
			24
			25
			26
			27
			28
			29
			30	Strings too long to fit are formatted like this
			31
			32
			33
			34
			35
			36
			37
			38
			39
			40
			41
			42
			43
			44
			45
			46
			47
			48
			49
			50
			51
			52
			53
			54
			55
			56
			57
			58
			59
			60
			61
			62
			63
			64
			65
			66
			67
			68
			69
			70
			71
			72
			73
			74
			75
			76
			77
			78
			79
			80
			81
			82
			83
			84
			85
			86
			87
			88
			89
			90
			91
			92
			93
			94
			95
			96
			97
			98
			99

## P_ValveSO
	P_ValveSO: Solenoid Operated Valve	Read From CLX:
		Send To CLX:

		Description:		Description for display on HMI	Label for graphic symbol displayed on HMI	Tagname for display on HMI	Process Area for security	1=Fail Open (energize to close), 0=Fail Closed (energize to open)	1=Valve provides an Open Limit Switch signal	1=Valve provides a Closed Limit Switch signal	1=Valve Open LS should be used for failure checking	1=Valve Closed LS should be used for failure checking	1=both switches ON=fail, 0=both switches OFF=fail		After command, time reach position before fault (sec)	Time to sound audible on commanded energize (sec) (0=disabled)	1=Stop Valve and Alarm on Full Stall; 0=Alarm only on Full Stall	1=Stop Valve and Alarm on Transit Stall; 0=Alarm only on Transit Stall	1=Stop Valve and Alarm on I/O Fault; 0=Alarm only on I/O Fault	Delay to echo back of Open/Closed status when in Simulation (sec)	1=Tells HMI a P_Perm is connected to Inp_Perm	1=Tells HMI a P_Intlk is connected to Inp_Intlk	1=Tells HMI a P_ValveStats is monitoring this valve	1=Tells HMI an object with more info is available	Full Stall Alarm Condition	Full Stall Alarm Tag	1=Full Stall Alarm exists and will be checked	1=Reset required to clear Full Stall Alarm	1=Acknowledge required for Full Stall Alarm	Full Stall Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	Transit Stall Alarm Condition	Transit Stall Alarm Tag	1=Transit Stall Alarm exists and will be checked	1=Reset required to clear Transit Stall Alarm	1=Acknowledge required for Transit Stall Alarm	Transit Stall Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	Interlock Tripped Alarm Condition	Interlock Tripped Alarm Tag	1=Interlock Tripped Alarm exists and will be checked	1=Reset required to clear Interlock Trip Alarm	1=Acknowledge required for Interlock Trip Alarm	Interlock Trip Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	I/O Fault Alarm Condition	I/O Fault Alarm Tag	1=I/O Fault Alarm exists and will be checked	1=Reset required to clear I/O Fault Alarm	1=Acknowledge required for I/O Fault Alarm	I/O Fault Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	1=New valve OCmd resets shed latches and cleared alarms, 0=OCmdReset reqd	1=New valve XCmd resets shed latches and cleared alarms, 0=OCmdReset reqd	1=Override ignores Bypassable Perm/ Intlk; 0=always use Perm/Intlk	1=Operator (unlocked) exists, can be selected	1=Operator Locked exists, can be selected	1=Program (unlocked) exists, can be selected	1=Program Locked exists, can be selected	1=External exists, can be selected	1=Maintenance exists, can be selected	1=Maintenance Out of Service exists, can be selected	1=Override supersedes Prog/Oper Lock, 0=don't override Lock	1=External supersedes Prog/Oper Lock, 0=don't override Lock	1=Power Up to Prog, 0=Power Up to Oper	Normal Source: 1=Program if no requests; 0=Operator if no requests	Command Priority: 1=Program Cmds Win; 0=Operator Cmds Win	1=PCmd_Prog used as a Level (1=Prog, 0=Oper)	1=PCmd_Lock used as a Level (1=Lock, 0=Unlock)	1=XCmd_Acq used as Level (1=Acq, 0=Rel)
		Usage:		Local	Local	Local	Local	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Local	Input	Input	Input	Local	Local	Local	Local	Local	Local	Local	Local
		Data Type:		STRING_40	STRING_20	STRING_20	STRING_Area	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	REAL	REAL	REAL	BOOL	BOOL	BOOL	REAL	BOOL	BOOL	BOOL	BOOL	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL
			(Origin)	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.FullStall.Cfg_	.FullStall.Cfg_	.FullStall.Cfg_	.FullStall.Cfg_	.FullStall.Cfg_	.FullStall.Cfg_	.FullStall.Cfg_	.FullStall.Cfg_	.TransitStall.Cfg_	.TransitStall.Cfg_	.TransitStall.Cfg_	.TransitStall.Cfg_	.TransitStall.Cfg_	.TransitStall.Cfg_	.TransitStall.Cfg_	.TransitStall.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.Cfg_	.Cfg_	.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_
Unit	Tag Description	TagName	Instance	Desc	Label	Tag	Area	FailOpen	HasOpenLS	HasClosedLS	UseOpenLS	UseClosedLS	LSFail	FullStallT	TransitStallT	StartHornT	ShedOnFullStall	ShedOnTransitStall	ShedOnIOFault	SimFdbkT	HasPermObj	HasIntlkObj	HasStatsObj	HasMoreObj	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	OCmdResets	XCmdResets	OvrdPermIntlk	HasOper	HasOperLocked	HasProg	HasProgLocked	HasExt	HasMaint	HasMOoS	OvrdOverLock	ExtOverLock	ProgPwrUp	ProgNormal	PCmdPriority	PCmdProgAsLevel	PCmdLockAsLevel	ExtAcqAsLevel
		Default Values:	0	Solenoid Operated Valve	Valve Control	P_ValveSO	area01	0	0	0	0	0	1	5	10	0	1	1	1	2	0	0	0	0	Full Stall	P_ValveSO.FullStall	0	0	1	1000	0	1	5	480	Transit Stall	P_ValveSO.TransitStall	0	0	1	1000	0	1	5	480	Interlock Trip	P_ValveSO.IntlkTrip	0	0	1	500	0	1	5	480	I/O Fault	P_ValveSO.IOFault	0	0	1	1000	0	1	5	480	0	0	0	1	1	1	1	0	1	1	1	0	0	0	0	0	0	0
		MyP_ValveSO	1	Ingr 1 Addition Line Block Valve	Ingr 1 Block Valve	XV4302	area01	1	1	1	1	1	1	10	30	0	0	0	0	5	1	1	1	0	Valve Full Stall	MyValveSO.FullStall	1	0	1	3	1	1	5	480	Valve Transit Stall	MyValveSO.TransitSta	1	0	1	3	1	1	5	480	Interlock Trip	MyValveSO.IntlkTrip	1	0	1	3	1	1	5	480	I/O Fault	MyValveSO.IOFault	1	0	1	3	1	1	5	480	0	0	0	1	1	1	1	0	1	1	1	0	0	0	0	0	0	0
			2
			3
			4
			5
			6
			7
			8
			9
			10
			11
			12
			13
			14
			15
			16
			17
			18
			19
			20
			21
			22
			23
			24
			25
			26
			27
			28
			29
			30	Strings too long to fit are formatted like this
			31
			32
			33
			34
			35
			36
			37
			38
			39
			40
			41
			42
			43
			44
			45
			46
			47
			48
			49
			50
			51
			52
			53
			54
			55
			56
			57
			58
			59
			60
			61
			62
			63
			64
			65
			66
			67
			68
			69
			70
			71
			72
			73
			74
			75
			76
			77
			78
			79
			80
			81
			82
			83
			84
			85
			86
			87
			88
			89
			90
			91
			92
			93
			94
			95
			96
			97
			98
			99

## P_ValveStats
	P_ValveStats: 2-State Valve Statistics	Read From CLX:
		Send To CLX:

		Description:		Description for display on HMI	Label for graphic symbol displayed on HMI	Tagname for display on HMI	Process Area for security	Descriptive text for Stopped / Other State	1=Valve has Stopped or other state(s) to be monitored	Maximum Time Opening (sec) before raising Sts_SlowOpen	Maximum Time Closing (sec) before raising Sts_SlowClose	1=Tells HMI an object with more info is available
		Usage:		Local	Local	Local	Local	Local	Input	Input	Input	Input
		Data Type:		STRING_40	STRING_20	STRING_20	STRING_Area	STRING_20	BOOL	REAL	REAL	BOOL
			(Origin)	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_
Unit	Tag Description	TagName	Instance	Desc	Label	Tag	Area	StopOtherDesc	HasStopOther	SlowOpenT	SlowCloseT	HasMoreObj
		Default Values:	0	Valve Statistics (stroke times, counts)	Valve Statistics	P_ValveStats	area01		0	10.0	10.0	0
		MyP_ValveStats	1	Valve Statistics (stroke times, counts)	Valve Statistics	P_ValveStats	area01	Stopped	0	10	10	0
			2
			3
			4
			5
			6
			7
			8
			9
			10
			11
			12
			13
			14
			15
			16
			17
			18
			19
			20
			21
			22
			23
			24
			25
			26
			27
			28
			29
			30	Strings too long to fit are formatted like this
			31
			32
			33
			34
			35
			36
			37
			38
			39
			40
			41
			42
			43
			44
			45
			46
			47
			48
			49
			50
			51
			52
			53
			54
			55
			56
			57
			58
			59
			60
			61
			62
			63
			64
			65
			66
			67
			68
			69
			70
			71
			72
			73
			74
			75
			76
			77
			78
			79
			80
			81
			82
			83
			84
			85
			86
			87
			88
			89
			90
			91
			92
			93
			94
			95
			96
			97
			98
			99

## P_VSD
	P_VSD: Variable Speed Drive	Read From CLX:
		Send To CLX:

		Description:		Description for display on HMI	Label for graphic symbol displayed on HMI	Tagname for display on HMI	Process Area for security	Name for Forward Direction, e.g., "Up", "Forward"	Name for Reverse Direction, e.g., "Down", "Reverse"	Speed Reference Engineering Units for display on HMI	Speed Reference Minimum in Drive (raw) Units (for scaling)	Speed Reference Maximum in Drive (raw) Units (for scaling)	Speed Reference Minimum in Engineering Units (for scaling)	Speed Reference Maximum in Engineering Units (for scaling)	Speed Feedback Engineering Units for display on HMI	Speed Feedback Minimum in Drive (raw) Units (for scaling)	Speed Feedback Maximum in Drive (raw) Units (for scaling)	Speed Feedback Minimum in Engineering Units (for scaling)	Speed Feedback Maximum in Engineering Units (for scaling)	Number of decimal places for speed ref/fdbk display (0..6)	1=Drive can be run reverse, 0=Forward only	1=Drive Jog Command enabled/visible, 0=Drive Jog Command not allowed	1=Drive provides speed feedback on Inp_SpeedFdbk	1=Drive speed determines running state, 0=state determined by drive Active input bit	1=Allow Local Start/Stop without alarm, 0=Start/Stop from HMI/prog only	Minimum Speed Reference in EU (for limiting)	Maximum Speed Reference in EU (for limiting)	Maximum jog time (sec, 0=unlimited)	Time to sound audible on commanded start (sec) (0=disabled)	Time to pulse Out_Reset to clear drive fault	1=Drive provides feedback signal on Inp_Running when running	1=Drive run feedback should be used for failure checking	Time after Start to get Run Feedback before Fault (sec)	Time after Stop to drop Run Feedback before Fault (sec)	1=Stop Motor and Alarm on Fail to Start; 0=Alarm only on Fail to Start	1=Stop Motor and Alarm on I/O Fault; 0=Alarm only on I/O Fault	Datalink Input Engineering Units for display on HMI	Datalink Input Label displayed on faceplate	1=A signal is connected to Inp_Datalink	Input Datalink Minimum in Drive (raw) Units (for scaling)	Input Datalink Maximum in Drive (raw) Units (for scaling)	Number of decimal places for Output Datalink display (0..6)	Input Datalink Minimum in Engineering Units (for scaling)	Input Datalink Maximum in Engineering Units (for scaling)	Datalink Output Engineering Units for display on HMI	Datalink Output Label displayed on faceplate	1=A signal is connected to Out_Datalink	Output Datalink Minimum in Drive (raw) Units (for scaling)	Output Datalink Maximum in Drive (raw) Units (for scaling)	Number of decimal places for Output Datalink display (0..6)	Output Datalink Minimum in Engineering Units (for scaling)	Output Datalink Maximum in Engineering Units (for scaling)	Minimum Output Datalink in EU (for limiting)	Maximum Output Datalink in EU (for limiting)	Time to ramp speed fdbk when in Simulation (sec)	1=In simulation, scale Speed Ref EU to Speed Fdbk EU	1=In simulation, scale Speed Ref EU to raw, then raw to Speed Fdbk EU	1=Tells HMI a P_Perm is connected to Inp_FwdPerm	1=Tells HMI a P_Perm is connected to Inp_RevPerm	1=Tells HMI a P_Intlk is connected to Intlk	1=Tells HMI a P_ReshInh Inhibit is connected	1=Tells HMI a P_RunTime is connected	1=Tells HMI an object with more info is available	Fail To Start Alarm Condition	Fail To Start Alarm Tag	1=Fail To Start Alarm exists and will be checked	1=Reset required to clear Fail To Start Alarm	1=Acknowledge required for Fail to Start Alarm	Fail To Start Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	Fail To Stop Alarm Condition	Fail To Stop Alarm Tag	1=Fail To Stop Alarm exists and will be checked	1=Reset required to clear Fail To Stop Alarm	1=Fail To Stop Alarm must be acknowledged	Fail To Stop Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	Interlock Tripped Alarm Condition	Interlock Tripped Alarm Tag	1=Interlock Tripped Alarm exists and will be checked	1=Reset required to clear Interlock Trip Alarm	1=Acknowledge required for Interlock Trip Alarm	Interlock Trip Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	Drive Fault Alarm Condition	Drive Fault Alarm Tag	1=Drive Fault Alarm exists and will be checked	1=Reset required to clear Drive Fault Alarm	1=Acknowledge required for Drive Fault Alarm	Drive Fault Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	I/O Fault Alarm Condition	I/O Fault Alarm Tag	1=I/O Fault Alarm exists and will be checked	1=Reset required to clear I/O Fault Alarm	1=Acknowledge required for I/O Fault Alarm	I/O Fault Alarm Severity: 1..250=Low, 251..500=Medium, 501..750=High, 751..1000=Urgent	1=Allow Operator to Shelve Alarm	1=Allow Maintenance to Disable Alarm	Minimum time Alm output stays on (sec)	Auto unshelve after shelved this long (min)	1=OCmd_Stop has priority, accepted any time, 0=OCmd_Stop only in Oper, Maint Mode.	1=XCmd_Stop any time, 0=XCmd_Stop only when Ext selected	1=New drive OCmd resets shed latches and cleared alarms, 0=OCmdReset reqd	1=New drive XCmd resets shed latches and cleared alarms, 0=XCmdReset reqd	1=Override ignores Bypassable Perm/ Intlk; 0=always use Perm/Intlk	1=PSets track OSets in Oper, OSets track PSets in Prog, 0=no tracking	1=Prog/Oper Settings track Override/Hand CV	Oper keeps control in Prog / Ext: .0=Reference, .1=Start/Stop, .3=OutDatalink	Prog keeps control in Oper / Ext: .0=Reference, .1=Start/Stop, .3=OutDatalink	Ext keeps control in Prog / Oper: .0=Reference, .1=Start/Stop, .3=OutDatalink	1=Operator (unlocked) exists, can be selected	1=Operator Locked exists, can be selected	1=Program (unlocked) exists, can be selected	1=Program Locked exists, can be selected	1=External exists, can be selected	1=Maintenance exists, can be selected	1=Maintenance Out of Service exists, can be selected	1=Override supersedes Prog/Oper Lock, 0=don't override Lock	1=External supersedes Prog/Oper Lock, 0=don't override Lock	1=Power Up to Prog, 0=Power Up to Oper	Normal Source: 1=Program if no requests; 0=Operator if no requests	Command Priority: 1=Program Cmds Win; 0=Operator Cmds Win	1=PCmd_Prog used as a Level (1=Prog, 0=Oper)	1=PCmd_Lock used as a Level (1=Lock, 0=Unlock)	1=XCmd_Acq used as Level (1=Acq, 0=Rel)
		Usage:		Local	Local	Local	Local	Local	Local	Local	Input	Input	Input	Input	Local	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Local	Local	Input	Input	Input	Input	Input	Input	Local	Local	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Local	Local	Local	Local	Local	Local	Local	Local	Input	Input	Input	Input	Input	Input	Input	Input	Input	Input	Local	Local	Local	Local	Local	Local	Local	Local
		Data Type:		STRING_40	STRING_20	STRING_20	STRING_Area	STRING_16	STRING_16	STRING_8	REAL	REAL	REAL	REAL	STRING_8	REAL	REAL	REAL	REAL	DINT	BOOL	BOOL	BOOL	BOOL	BOOL	REAL	REAL	REAL	REAL	REAL	BOOL	BOOL	REAL	REAL	BOOL	BOOL	STRING_8	STRING_20	BOOL	REAL	REAL	DINT	REAL	REAL	STRING_8	STRING_20	BOOL	REAL	REAL	DINT	REAL	REAL	REAL	REAL	REAL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	STRING_20	STRING_20	BOOL	BOOL	BOOL	DINT	BOOL	BOOL	DINT	DINT	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	SINT	SINT	SINT	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL	BOOL
			(Origin)	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.FailToStart.Cfg_	.FailToStart.Cfg_	.FailToStart.Cfg_	.FailToStart.Cfg_	.FailToStart.Cfg_	.FailToStart.Cfg_	.FailToStart.Cfg_	.FailToStart.Cfg_	.FailToStop.Cfg_	.FailToStop.Cfg_	.FailToStop.Cfg_	.FailToStop.Cfg_	.FailToStop.Cfg_	.FailToStop.Cfg_	.FailToStop.Cfg_	.FailToStop.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.IntlkTrip.Cfg_	.DriveFault.Cfg_	.DriveFault.Cfg_	.DriveFault.Cfg_	.DriveFault.Cfg_	.DriveFault.Cfg_	.DriveFault.Cfg_	.DriveFault.Cfg_	.DriveFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.IOFault.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_	.CmdSrc.Cfg_
Unit	Tag Description	TagName	Instance	Desc	Label	Tag	Area	FwdText	RevText	SpeedRefEU	SpeedRefRawMin	SpeedRefRawMax	SpeedRefEUMin	SpeedRefEUMax	SpeedFdbkEU	SpeedFdbkRawMin	SpeedFdbkRawMax	SpeedFdbkEUMin	SpeedFdbkEUMax	DecPlcs	HasReverse	HasJog	HasSpeedFdbk	UseSpeedFdbk	AllowLocal	MinSpdRef	MaxSpdRef	MaxJogT	StartHornT	ResetPulseT	HasRunFdbk	UseRunFdbk	FailToStartT	FailToStopT	ShedOnFailToStart	ShedOnIOFault	InpDatalinkEU	InpDatalinkLabel	HasInpDatalink	InpDatalinkRawMin	InpDatalinkRawMax	InpDLDecPlcs	InpDatalinkEUMin	InpDatalinkEUMax	OutDatalinkEU	OutDatalinkLabel	HasOutDatalink	OutDatalinkRawMin	OutDatalinkRawMax	OutDLDecPlcs	OutDatalinkEUMin	OutDatalinkEUMax	OutDatalinkMin	OutDatalinkMax	SimRampT	SimScaleEU	SimScaleRaw	HasFwdPermObj	HasRevPermObj	HasIntlkObj	HasResInhObj	HasRunTimeObj	HasMoreObj	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	Cond	Tag	Exists	ResetReqd	AckReqd	Severity	AllowShelve	AllowDisable	AlmMinOnT	MaxShelfT	OperStopPrio	ExtStopPrio	OCmdResets	XCmdResets	OvrdPermIntlk	SetTrack	SetTrackOvrdHand	OperKeep	ProgKeep	ExtKeep	HasOper	HasOperLocked	HasProg	HasProgLocked	HasExt	HasMaint	HasMOoS	OvrdOverLock	ExtOverLock	ProgPwrUp	ProgNormal	PCmdPriority	PCmdProgAsLevel	PCmdLockAsLevel	ExtAcqAsLevel
		Default Values:	0	Variable Speed Drive	Motor Speed Control	P_VSD	area01	Forward	Reverse	Hz	0	32767	0.0	130.0	Hz	0	32767	0.0	130.0	0	0	0	0	0	0	0.0	60.0	0.0	0	2	0	0	15	15	1	1			0	0	4095	2	0.0	409.5			0	0	4095	2	0.0	409.5	0.0	100.0	10	0	0	0	0	0	0	0	0	Failed to Start	P_VSD.FailToStart	0	0	1	1000	0	1	5	480	Failed to Stop	P_VSD.FailToStop	0	0	1	1000	0	1	5	480	Interlock Trip	P_VSD.IntlkTrip	0	0	1	500	0	1	5	480	Drive Fault	P_VSD.DriveFault	0	0	1	1000	0	1	5	480	I/O Fault	P_VSD.IOFault	0	0	1	1000	0	1	5	480	0	0	0	0	0	1	0	0	0	0	1	1	1	1	0	1	1	1	0	0	0	0	0	0	0
		MyP_VSD	1	Reactor #1 Agitator Speed Control	Agitator Speed	MyDrive	area01	Forward	Reverse	Hz	0	32767	0	130	Hz	0	32767	0	130	2	0	0	0	0	0	0	60	0	0	2	0	0	15	15	1	1	Amps	Torque Current	0	0	4095	2	0	409.5	Hz	Jog Speed	0	0	4095	2	0	409.5	0	100	10	0	0	0	0	0	0	0	0	Failed to Start	MyDrive.FailToStart	0	0	1	1000	1	1	5	480	Failed to Stop	MyDrive.FailToStop	0	0	1	1000	1	1	5	480	Interlock Trip	MyDrive.IntlkTrip	0	0	1	500	1	1	5	480	Drive Fault	MyDrive.DriveFault	0	0	1	1000	1	1	5	480	I/O Fault	MyDrive.IOFault	0	0	1	1000	1	1	5	480	0	0	0	0	0	1	0	0	0	0	1	1	1	1	0	1	1	1	0	0	0	0	0	0	0
			2
			3
			4
			5
			6
			7
			8
			9
			10
			11
			12
			13
			14
			15
			16
			17
			18
			19
			20
			21
			22
			23
			24
			25
			26
			27
			28
			29
			30	Strings too long to fit are formatted like this
	NOTE:		31
	Drive Fault Code numbers and		32
	corresponding Fault Descriptions are		33
	stored in a separate Tag. Use the Drive		34
	Fault Code Tool to read / save / restore		35
	those values.		36
			37
			38
			39
			40
			41
			42
			43
			44
			45
			46
			47
			48
			49
			50
			51
			52
			53
			54
			55
			56
			57
			58
			59
			60
			61
			62
			63
			64
			65
			66
			67
			68
			69
			70
			71
			72
			73
			74
			75
			76
			77
			78
			79
			80
			81
			82
			83
			84
			85
			86
			87
			88
			89
			90
			91
			92
			93
			94
			95
			96
			97
			98
			99

## E300_TripCodeList
	E300_TripCodeList	Read From CLX:
		Send To CLX:
	Trip codes and text for
	E300 Overload Relays	Description:		Fault Code	Description for given Trip Code
		Usage:		UDT	UDT
		Data Type:		DINT	STRING_40
			(Origin)	.	.
Unit	Tag Description	TagName	Instance	Code	Desc
		Default Values:	0	0	Check drive manual for this fault code
		E300_TripCodeList[0]	1	0	No Trip Conditions Detected
		E300_TripCodeList[1]	2	1	Motor overcurrent trip
		E300_TripCodeList[2]	3	2	Motor phase loss trip
		E300_TripCodeList[3]	4	3	Ground fault trip
		E300_TripCodeList[4]	5		Motor stall (fail to reach speed) trip
		E300_TripCodeList[5]	6	5	Motor current over jam trip limit
		E300_TripCodeList[6]	7	6	Motor current below operating point trip
		E300_TripCodeList[7]	8	7	Phase-to-phase current imbalance trip
		E300_TripCodeList[8]	9	8	L1 undercurrent trip
		E300_TripCodeList[9]	10	9	L2 undercurrent trip
		E300_TripCodeList[10]	11	10	L3 undercurrent trip
		E300_TripCodeList[11]	12	11	L1 overcurrent trip
		E300_TripCodeList[12]	13	12	L2 overcurrent trip
		E300_TripCodeList[13]	14	13	L3 overcurrent trip
		E300_TripCodeList[14]	15	14	L1 current loss trip
		E300_TripCodeList[15]	16	15	L2 current loss trip
		E300_TripCodeList[16]	17	16	L3 current loss trip
		E300_TripCodeList[17]	18	17	Line-to-line undervoltage trip
		E300_TripCodeList[18]	19	18	Line-to line overvoltage trip
		E300_TripCodeList[19]	20	19	Phase-to-phase voltage imbalance trip
		E300_TripCodeList[20]	21	20	Supply voltage phases rotated
		E300_TripCodeList[21]	22	21	Low line frequency trip
		E300_TripCodeList[22]	23	22	High line frequency trip
		E300_TripCodeList[23]	24	25	Sensing module firmware failed to load
		E300_TripCodeList[24]	25	26	Sensing Module output enable open trip
		E300_TripCodeList[25]	26	27	Sensing Module missing interrupts trip
		E300_TripCodeList[26]	27	28	Sensing Module not calibrated trip
		E300_TripCodeList[27]	28	29	Sensing Module frame type failure trip
		E300_TripCodeList[28]	29	30	Sensing Module configuration failure
		E300_TripCodeList[29]	30	31	Sensing Module overrun error trip
		E300_TripCodeList[30]	31	32	Sensing Module not responding trip
		E300_TripCodeList[31]	32	33	Low total real power (kW) trip
		E300_TripCodeList[32]	33	34	High total real power (kW) trip
		E300_TripCodeList[33]	34	35	Low reactive pwr consumed (+kVAR) trip
		E300_TripCodeList[34]	35	36	High reactive pwr consumed (+kVAR) trip
		E300_TripCodeList[35]	36	37	Low reactive pwr generated (-kVAR) trip
		E300_TripCodeList[36]	37	38	High reactive pwr generated (-kVAR) trip
		E300_TripCodeList[37]	38	39	Low apparent power (kVA) trip
		E300_TripCodeList[38]	39	40	High apparent power (kVA) trip
		E300_TripCodeList[39]	40	41	Low power factor lagging (-PF) trip
		E300_TripCodeList[40]	41	42	High power factor lagging (-PF) trip
		E300_TripCodeList[41]	42	43	Low power factor leading (+PF) trip
		E300_TripCodeList[42]	43	44	High power factor leading (+PF) trip
		E300_TripCodeList[43]	44	49	Test trip (held Test/Reset button)
		E300_TripCodeList[44]	45	50	Motor stator windings overheated
		E300_TripCodeList[45]	46	51	DeviceLogix defined trip was generated
		E300_TripCodeList[46]	47	52	Stop button pressed at Operator Station
		E300_TripCodeList[47]	48	53	Remote trip commanded
		E300_TripCodeList[48]	49	54	Maximum starts per hour exceeded
		E300_TripCodeList[49]	50	55	Hardware config. fault, check inputs
		E300_TripCodeList[50]	51	58	DeviceLogix feedback timeout trip
		E300_TripCodeList[51]	52	59	Control Module CAN0 init failure
		E300_TripCodeList[52]	53	60	Control Module CAN0 bus failure
		E300_TripCodeList[53]	54	61	Control Module CAN1 init failure
		E300_TripCodeList[54]	55	62	Control Module CAN1 bus failure
		E300_TripCodeList[55]	56	63	Control Module ADC0 failure trip
		E300_TripCodeList[56]	57	64	Control Module CRC error count trip
		E300_TripCodeList[57]	58	65	Analog module 1 channel 00 trip
		E300_TripCodeList[58]	59	66	Analog module 1 channel 01 trip
		E300_TripCodeList[59]	60	67	Analog module 1 channel 02 trip
		E300_TripCodeList[60]	61	68	Analog module 2 channel 00 trip
		E300_TripCodeList[61]	62	69	Analog module 2 channel 01 trip
		E300_TripCodeList[62]	63	70	Analog module 2 channel 02 trip
		E300_TripCodeList[63]	64	71	Analog module 3 channel 00 trip
		E300_TripCodeList[64]	65	72	Analog module 3 channel 01 trip
		E300_TripCodeList[65]	66	73	Analog module 3 channel 02 trip
		E300_TripCodeList[66]	67	74	Analog module 4 channel 00 trip
		E300_TripCodeList[67]	68	75	Analog module 4 channel 01 trip
		E300_TripCodeList[68]	69	76	Analog module 4 channel 02 trip
		E300_TripCodeList[69]	70	77	Ext. NVS Chip comms timeout trip
		E300_TripCodeList[70]	71	78	Ext. NVS CRC error trip
		E300_TripCodeList[71]	72	79	Ext. NVS Chip data out of range trip
		E300_TripCodeList[72]	73	81	Digital exp. module 1 malfunction trip
		E300_TripCodeList[73]	74	82	Digital exp. module 2 malfunction trip
		E300_TripCodeList[74]	75	83	Digital exp. module 3 malfunction trip
		E300_TripCodeList[75]	76	84	Digital exp. module 4 malfunction trip
		E300_TripCodeList[76]	77	85	Analog exp. module 1 malfunction trip
		E300_TripCodeList[77]	78	86	Analog exp. module 2 malfunction trip
		E300_TripCodeList[78]	79	87	Analog exp. module 3 malfunction trip
		E300_TripCodeList[79]	80	88	Analog exp. module 4 malfunction trip
		E300_TripCodeList[80]	81	90	Control module type mismatch trip
		E300_TripCodeList[81]	82	91	Sensing module type mismatch trip
		E300_TripCodeList[82]	83	92	Communication module type mismatch trip
		E300_TripCodeList[83]	84	93	Operator station type mismatch trip
		E300_TripCodeList[84]	85	94	Digital I/O module type mismatch trip
		E300_TripCodeList[85]	86	95	Analog I/O module type mismatch trip
		E300_TripCodeList[86]	87	96	Current/voltage detected in Test Mode
		E300_TripCodeList[87]	88	97	Heap memory could not be allocated
		E300_TripCodeList[88]	89	98	Vendor ID hardware fault

## E300_WarningCodeList
	E300_WarningCodeList	Read From CLX:
		Send To CLX:
	Warning codes and text for
	E300 Overload Relays	Description:		Fault Code	Description for given Warning Code
		Usage:		UDT	UDT
		Data Type:		DINT	STRING_40
			(Origin)	.	.
Unit	Tag Description	TagName	Instance	Code	Desc
		Default Values:	0	0	Check drive manual for this fault code
		E300_WarningCodeList[0]	1	0	No warnings
		E300_WarningCodeList[1]	2	1	Approaching motor current overload
		E300_WarningCodeList[2]	3	3	Motor lead or winding ground fault
		E300_WarningCodeList[3]	4	5	Motor current over jam warning limit
		E300_WarningCodeList[4]	5		Motor below normal operating current
		E300_WarningCodeList[5]	6	7	Phase-t0-phase current imbalance warning
		E300_WarningCodeList[6]	7	8	L1 undercurrent warning
		E300_WarningCodeList[7]	8	9	L2 undercurrent warning
		E300_WarningCodeList[8]	9	10	L3 undercurrent warning
		E300_WarningCodeList[9]	10	11	L1 overcurrent warning
		E300_WarningCodeList[10]	11	12	L2 overcurrent warning
		E300_WarningCodeList[11]	12	13	L3 overcurrent warning
		E300_WarningCodeList[12]	13	14	L1 current loss warning
		E300_WarningCodeList[13]	14	15	L2 current loss warning
		E300_WarningCodeList[14]	15	16	L3 current loss warning
		E300_WarningCodeList[15]	16	17	Line-to-line undervoltage warning
		E300_WarningCodeList[16]	17	18	Line-to-line overvoltage warning
		E300_WarningCodeList[17]	18	19	Phase-to-phase voltage imbalance warning
		E300_WarningCodeList[18]	19	20	Supply voltage phases rotated warning
		E300_WarningCodeList[19]	20	21	Low line frequency warning
		E300_WarningCodeList[20]	21	22	High line frequency warning
		E300_WarningCodeList[21]	22	33	Low total real power (kW) warning
		E300_WarningCodeList[22]	23	34	High total real power (kW) warning
		E300_WarningCodeList[23]	24	35	Low reactive pwr consumed (+kVAR) warn
		E300_WarningCodeList[24]	25	36	High reactive pwr consumed (+kVAR) warn
		E300_WarningCodeList[25]	26	37	Low reactive pwr generated (-kVAR) warn
		E300_WarningCodeList[26]	27	38	High reactive pwr generated (-kVAR) warn
		E300_WarningCodeList[27]	28	39	Low apparent power (kVA) warning
		E300_WarningCodeList[28]	29	40	High apparent power (kVA) warning
		E300_WarningCodeList[29]	30	41	Low power factor lagging (-PF) warning
		E300_WarningCodeList[30]	31	42	High power factor lagging (-PF) warning
		E300_WarningCodeList[31]	32	43	Low power factor leading (+PF) warning
		E300_WarningCodeList[32]	33	44	High power factor leading (+PF) warning
		E300_WarningCodeList[33]	34	50	Motor stator windings overheated (PTC)
		E300_WarningCodeList[34]	35	51	DeviceLogix defined warning
		E300_WarningCodeList[35]	36	56	Config Error, see par. 38-39 for reason
		E300_WarningCodeList[36]	37	58	DeviceLogix feedback timeout trip
		E300_WarningCodeList[37]	38	60	Number of starts warning
		E300_WarningCodeList[38]	39	61	Operating hours warning
		E300_WarningCodeList[39]	40	65	Analog module 1 channel 00 warning
		E300_WarningCodeList[40]	41	66	Analog module 1 channel 01 warning
		E300_WarningCodeList[41]	42	67	Analog module 1 channel 02 warning
		E300_WarningCodeList[42]	43	68	Analog module 2 channel 00 warning
		E300_WarningCodeList[43]	44	69	Analog module 2 channel 01 warning
		E300_WarningCodeList[44]	45	70	Analog module 2 channel 02 warning
		E300_WarningCodeList[45]	46	71	Analog module 3 channel 00 warning
		E300_WarningCodeList[46]	47	72	Analog module 3 channel 01 warning
		E300_WarningCodeList[47]	48	73	Analog module 3 channel 02 warning
		E300_WarningCodeList[48]	49	74	Analog module 4 channel 00 warning
		E300_WarningCodeList[49]	50	75	Analog module 4 channel 01 warning
		E300_WarningCodeList[50]	51	76	Analog module 4 channel 02 warning
		E300_WarningCodeList[51]	52	81	Digital expansion module 1 malfunction
		E300_WarningCodeList[52]	53	82	Digital expansion module 2 malfunction
		E300_WarningCodeList[53]	54	83	Digital expansion module 3 malfunction
		E300_WarningCodeList[54]	55	84	Digital expansion module 4 malfunction
		E300_WarningCodeList[55]	56	85	Analog expansion module 1 malfunction
		E300_WarningCodeList[56]	57	86	Analog expansion module 2 malfunction
		E300_WarningCodeList[57]	58	87	Analog expansion module 3 malfunction
		E300_WarningCodeList[58]	59	88	Analog expansion module 4 malfunction
		E300_WarningCodeList[59]	60	90	Control module type mismatch
		E300_WarningCodeList[60]	61	91	Sensing module type mismatch
		E300_WarningCodeList[61]	62	92	Communication module type mismatch
		E300_WarningCodeList[62]	63	93	Operator station type mismatch
		E300_WarningCodeList[63]	64	94	Digital I/O module type mismatch
		E300_WarningCodeList[64]	65	95	Analog I/O module type mismatch
		E300_WarningCodeList[65]	66	98	Hardware fault

## PF4xx
	PF4xx_FaultCodeList	Read From CLX:
		Send To CLX:
	Fault codes and text for
	PowerFlex 4, 40, 400 series drives	Description:		Fault Code	Description for given Fault Code
		Usage:		UDT	UDT
		Data Type:		DINT	STRING_40
			(Origin)	.	.
Unit	Tag Description	TagName	Instance	Code	Desc
		Default Values:	0	0	Check drive manual for this fault code
		PF4xx_FaultCodeList[0]	1	0	Check drive manual for this fault code
		PF4xx_FaultCodeList[1]	2	71	Network Loss
		PF4xx_FaultCodeList[2]	3	81	Communication Loss
		PF4xx_FaultCodeList[3]	4	111	Enable Hardware
		PF4xx_FaultCodeList[4]	5		SW OverCurrent
		PF4xx_FaultCodeList[5]	6	64	Drive Overload
		PF4xx_FaultCodeList[6]	7	2	Auxiliary Input
		PF4xx_FaultCodeList[7]	8	3	Power Loss
		PF4xx_FaultCodeList[8]	9	4	Under Voltage
		PF4xx_FaultCodeList[9]	10	5	Over Voltage
		PF4xx_FaultCodeList[10]	11	6	Motor Stalled
		PF4xx_FaultCodeList[11]	12	7	Motor Overload
		PF4xx_FaultCodeList[12]	13	8	Heatsink OverTemp
		PF4xx_FaultCodeList[13]	14	12	Hardware Overcurrent
		PF4xx_FaultCodeList[14]	15	13	Ground Fault
		PF4xx_FaultCodeList[15]	16	15	Load Loss
		PF4xx_FaultCodeList[16]	17	17	Input Phase Loss
		PF4xx_FaultCodeList[17]	18	29	Analog Input Loss
		PF4xx_FaultCodeList[18]	19	32	Fan Feedback Loss
		PF4xx_FaultCodeList[19]	20	33	Auto Restart Tries
		PF4xx_FaultCodeList[20]	21	38	Phase U to Ground
		PF4xx_FaultCodeList[21]	22	39	Phase V to Ground
		PF4xx_FaultCodeList[22]	23	40	Phase W to Ground
		PF4xx_FaultCodeList[23]	24	41	Phase U-V Short
		PF4xx_FaultCodeList[24]	25	42	Phase U-W Short
		PF4xx_FaultCodeList[25]	26	43	Phase V-W Short
		PF4xx_FaultCodeList[26]	27	48	Params Defaulted
		PF4xx_FaultCodeList[27]	28	70	Power Unit Fault
		PF4xx_FaultCodeList[28]	29	80	SVC AutoTune
		PF4xx_FaultCodeList[29]	30	91	Encoder Loss
		PF4xx_FaultCodeList[30]	31	94	Function Loss
		PF4xx_FaultCodeList[31]	32	100	Parameter Checksum
		PF4xx_FaultCodeList[32]	33	122	I/O Board Failure

## PF525
	PF525_FaultCodeList	Read From CLX:
		Send To CLX:
	Fault codes and text for
	PowerFlex 525 series drives	Description:		Fault Code	Description for given Fault Code
		Usage:		UDT	UDT
		Data Type:		DINT	STRING_40
			(Origin)	.	.
Unit	Tag Description	TagName	Instance	Code	Desc
		Default Values:	0	0	Check drive manual for this fault code
		PF525_FaultCodeList[0]	1	0	Check drive manual for this fault code
		PF525_FaultCodeList[1]	2	71	DSI Net Loss
		PF525_FaultCodeList[2]	3	72	Opt Net Loss
		PF525_FaultCodeList[3]	4	81	DSI Comm Loss
		PF525_FaultCodeList[4]	5		Opt Comm Loss
		PF525_FaultCodeList[5]	6	73	Ethernet Net Loss
		PF525_FaultCodeList[6]	7	83	Ethernet Comm Loss
		PF525_FaultCodeList[7]	8	111	Safety Hardware
		PF525_FaultCodeList[8]	9	59	Safety Open
		PF525_FaultCodeList[9]	10	63	SW Over Current
		PF525_FaultCodeList[10]	11	64	Drive Overload
		PF525_FaultCodeList[11]	12	2	Auxiliary Input
		PF525_FaultCodeList[12]	13	3	Power Loss
		PF525_FaultCodeList[13]	14	4	Under Voltage
		PF525_FaultCodeList[14]	15	5	Over Voltage
		PF525_FaultCodeList[15]	16	6	Motor Stalled
		PF525_FaultCodeList[16]	17	7	Motor Overload
		PF525_FaultCodeList[17]	18	8	Heatsink Overtemp
		PF525_FaultCodeList[18]	19	9	CC OverTemp
		PF525_FaultCodeList[19]	20	80	AutoTune Failure
		PF525_FaultCodeList[20]	21	12	Hardware Overcurrent
		PF525_FaultCodeList[21]	22	13	Ground Fault
		PF525_FaultCodeList[22]	23	15	Load Loss
		PF525_FaultCodeList[23]	24	21	Output Phase Loss
		PF525_FaultCodeList[24]	25	29	Analog Input Loss
		PF525_FaultCodeList[25]	26	33	Auto Restart Tries
		PF525_FaultCodeList[26]	27	38	Phase U to Ground
		PF525_FaultCodeList[27]	28	39	Phase V to Ground
		PF525_FaultCodeList[28]	29	40	Phase W to Ground
		PF525_FaultCodeList[29]	30	41	Phase U-V Short
		PF525_FaultCodeList[30]	31	42	Phase U-W Short
		PF525_FaultCodeList[31]	32	43	Phase V-W Short
		PF525_FaultCodeList[32]	33	70	Power Unit
		PF525_FaultCodeList[33]	34	91	Encoder Loss
		PF525_FaultCodeList[34]	35	94	Function Loss
		PF525_FaultCodeList[35]	36	100	Parameter Checksum
		PF525_FaultCodeList[36]	37	101	External Storage
		PF525_FaultCodeList[37]	38	105	C Connect Error
		PF525_FaultCodeList[38]	39	106	Incompat. C-P
		PF525_FaultCodeList[39]	40	107	Replaced C-P
		PF525_FaultCodeList[40]	41	109	Mismatch C-P
		PF525_FaultCodeList[41]	42	110	Keypad Membrane
		PF525_FaultCodeList[42]	43	48	Parameters Defaulted
		PF525_FaultCodeList[43]	44	114	uC Failure
		PF525_FaultCodeList[44]	45	122	I/O Baord Fail
		PF525_FaultCodeList[45]	46	125	Flash Update Reqd
		PF525_FaultCodeList[46]	47	126	Unrecoverable Error
		PF525_FaultCodeList[47]	48	127	DSI Flash Update Reqd

## PF6000_FW5
	PF6000_FW5_FaultCodeList	Read From CLX:
		Send To CLX:
	Fault codes and text for
	PowerFlex 6000 series MV drives	Description:		Fault Code	Description for given Fault Code
		Usage:		UDT	UDT
		Data Type:		DINT	STRING_40
			(Origin)	.	.
Unit	Tag Description	TagName	Instance	Code	Desc
		Default Values:	0	0	Check drive manual for this fault code
		PF6000_FW5_FaultCodeList[0]	1	0	Check drive manual for this fault code
		PF6000_FW5_FaultCodeList[1]	2	-1	No more fault information found
		PF6000_FW5_FaultCodeList[2]	3	654	DCS Communication Fault
		PF6000_FW5_FaultCodeList[3]	4	655	DCS Communication Fault Warn
		PF6000_FW5_FaultCodeList[4]	5		Input Circuit Breaker Tripped
		PF6000_FW5_FaultCodeList[5]	6	642	Transformer Over Temperature Trip
		PF6000_FW5_FaultCodeList[6]	7	643	Transformer Over Temperature Warn
		PF6000_FW5_FaultCodeList[7]	8	644	Power Module Cabinet Fan Fault
		PF6000_FW5_FaultCodeList[8]	9	645	Power Module Cabinet Fan CB Open
		PF6000_FW5_FaultCodeList[9]	10	646	Transformer Cabinet Fan Fault
		PF6000_FW5_FaultCodeList[10]	11	647	Transformer Cabinet Fan CB Open
		PF6000_FW5_FaultCodeList[11]	12	648	Auxiliary Power Off
		PF6000_FW5_FaultCodeList[12]	13	649	Cabinet Door Open
		PF6000_FW5_FaultCodeList[13]	14	650	Control Power Switch Warn
		PF6000_FW5_FaultCodeList[14]	15	651	Analog Loss Warn
		PF6000_FW5_FaultCodeList[15]	16	652	DSP Communication Fault
		PF6000_FW5_FaultCodeList[16]	17	653	Cooling Fan Contactor Open
		PF6000_FW5_FaultCodeList[17]	18	656	Feedback Analog Loss Warning
		PF6000_FW5_FaultCodeList[18]	19	433	Output Short Circuit
		PF6000_FW5_FaultCodeList[19]	20	434	Output Over Current
		PF6000_FW5_FaultCodeList[20]	21	435	Motor Over Temperature
		PF6000_FW5_FaultCodeList[21]	22	436	Output Over Voltage
		PF6000_FW5_FaultCodeList[22]	23	437	Abnormal Output Voltage
		PF6000_FW5_FaultCodeList[23]	24	438	Ground Fault
		PF6000_FW5_FaultCodeList[24]	25	439	Over Speed Fault
		PF6000_FW5_FaultCodeList[25]	26	440	Motor Stalled
		PF6000_FW5_FaultCodeList[26]	27	442	Output Phase Over Current
		PF6000_FW5_FaultCodeList[27]	28	449	Motor Over Temperature Warn
		PF6000_FW5_FaultCodeList[28]	29	450	Abnormal Output Voltage Warn
		PF6000_FW5_FaultCodeList[29]	30	451	Ground Fault Warn
		PF6000_FW5_FaultCodeList[30]	31	452	Output Frequency Deviation Warn
		PF6000_FW5_FaultCodeList[31]	32	454	Input Power Loss, Waiting For Recovery
		PF6000_FW5_FaultCodeList[32]	33	455	Input Voltage Sag, Derating Operating
		PF6000_FW5_FaultCodeList[33]	34	456	Low Voltage Ride Through Operating
		PF6000_FW5_FaultCodeList[34]	35	457	Input Voltage Sag, Flux Controlling
		PF6000_FW5_FaultCodeList[35]	36	458	Lower Ver., No PowerCell Bypass Function
		PF6000_FW5_FaultCodeList[36]	37	459	Bypass Operating
		PF6000_FW5_FaultCodeList[37]	38	465	Cabinet Door Open While Drive Energized
		PF6000_FW5_FaultCodeList[38]	39	466	E-Stop Trip
		PF6000_FW5_FaultCodeList[39]	40	467	Input CB Open (Not Initiated by Drive)
		PF6000_FW5_FaultCodeList[40]	41	468	Non-Zero Frequency Command Upon Start
		PF6000_FW5_FaultCodeList[41]	42	469	Flying Start Failed
		PF6000_FW5_FaultCodeList[42]	43	474	System Locked
		PF6000_FW5_FaultCodeList[43]	44	475	CPU Board In Wrong Position
		PF6000_FW5_FaultCodeList[44]	45	476	AT Board In Wrong Position
		PF6000_FW5_FaultCodeList[45]	46	477	5V Power Supply Fault
		PF6000_FW5_FaultCodeList[46]	47	478	15V Power Supply Fault
		PF6000_FW5_FaultCodeList[47]	48	479	24V DCS Power Supply Fault
		PF6000_FW5_FaultCodeList[48]	49	480	24V PLC Power Supply Fault
		PF6000_FW5_FaultCodeList[49]	50	481	PWMA Board In Wrong Position
		PF6000_FW5_FaultCodeList[50]	51	482	PWMB Board In Wrong Position
		PF6000_FW5_FaultCodeList[51]	52	483	PWMC Board In Wrong Position
		PF6000_FW5_FaultCodeList[52]	53	484	DT Board In Wrong Position
		PF6000_FW5_FaultCodeList[53]	54	486	Low Voltage Ride Through Over Time Limit
		PF6000_FW5_FaultCodeList[54]	55	487	Low Voltage Ride Through Short Interval
		PF6000_FW5_FaultCodeList[55]	56	488	Low Voltage Ride Through Failure
		PF6000_FW5_FaultCodeList[56]	57	489	Input Voltage Loss While Stop
		PF6000_FW5_FaultCodeList[57]	58	490	Input Voltage Loss Over Time Limit
		PF6000_FW5_FaultCodeList[58]	59	492	Input Voltage Loss
		PF6000_FW5_FaultCodeList[59]	60	493	Bypass Over Time Limit
		PF6000_FW5_FaultCodeList[60]	61	494	Bypass Start Failure
		PF6000_FW5_FaultCodeList[61]	62	561	Overtemp Time Out In Power Cell #1
		PF6000_FW5_FaultCodeList[62]	63	562	Overtemp Time Out In Power Cell #2
		PF6000_FW5_FaultCodeList[63]	64	563	Overtemp Time Out In Power Cell #3
		PF6000_FW5_FaultCodeList[64]	65	564	Overtemp Time Out In Power Cell #4
		PF6000_FW5_FaultCodeList[65]	66	565	Overtemp Time Out In Power Cell #5
		PF6000_FW5_FaultCodeList[66]	67	566	Overtemp Time Out In Power Cell #6
		PF6000_FW5_FaultCodeList[67]	68	567	Overtemp Time Out In Power Cell #7
		PF6000_FW5_FaultCodeList[68]	69	568	Overtemp Time Out In Power Cell #8
		PF6000_FW5_FaultCodeList[69]	70	569	Overtemp Time Out In Power Cell #9
		PF6000_FW5_FaultCodeList[70]	71	570	Overtemp Time Out In Power Cell #10
		PF6000_FW5_FaultCodeList[71]	72	571	Overtemp Time Out In Power Cell #11
		PF6000_FW5_FaultCodeList[72]	73	572	Overtemp Time Out In Power Cell #12
		PF6000_FW5_FaultCodeList[73]	74	573	Overtemp Time Out In Power Cell #13
		PF6000_FW5_FaultCodeList[74]	75	574	Overtemp Time Out In Power Cell #14
		PF6000_FW5_FaultCodeList[75]	76	575	Overtemp Time Out In Power Cell #15
		PF6000_FW5_FaultCodeList[76]	77	576	Overtemp Time Out In Power Cell #16
		PF6000_FW5_FaultCodeList[77]	78	577	Overtemp Time Out In Power Cell #17
		PF6000_FW5_FaultCodeList[78]	79	578	Overtemp Time Out In Power Cell #18
		PF6000_FW5_FaultCodeList[79]	80	579	Overtemp Time Out In Power Cell #19
		PF6000_FW5_FaultCodeList[80]	81	580	Overtemp Time Out In Power Cell #20
		PF6000_FW5_FaultCodeList[81]	82	581	Overtemp Time Out In Power Cell #21
		PF6000_FW5_FaultCodeList[82]	83	582	Overtemp Time Out In Power Cell #22
		PF6000_FW5_FaultCodeList[83]	84	583	Overtemp Time Out In Power Cell #23
		PF6000_FW5_FaultCodeList[84]	85	584	Overtemp Time Out In Power Cell #24
		PF6000_FW5_FaultCodeList[85]	86	585	Overtemp Time Out In Power Cell #25
		PF6000_FW5_FaultCodeList[86]	87	586	Overtemp Time Out In Power Cell #26
		PF6000_FW5_FaultCodeList[87]	88	587	Overtemp Time Out In Power Cell #27
		PF6000_FW5_FaultCodeList[88]	89	1	IGBT Over Current In Power Cell #1
		PF6000_FW5_FaultCodeList[89]	90	2	Capacitor Abnormal In Power Cell #1
		PF6000_FW5_FaultCodeList[90]	91	3	Input Over Voltage In Power Cell #1
		PF6000_FW5_FaultCodeList[91]	92	4	DCBus Undervolt In Power Cell #1 Warn
		PF6000_FW5_FaultCodeList[92]	93	5	Communication Error In Power Cell #1
		PF6000_FW5_FaultCodeList[93]	94	6	No PWM Pulse For IGBT In Power cell #1
		PF6000_FW5_FaultCodeList[94]	95	9	IGBT Failed To Turn On In Power Cell #1
		PF6000_FW5_FaultCodeList[95]	96	10	Power Cell #1 Bypassed
		PF6000_FW5_FaultCodeList[96]	97	11	Over Temperature In Power Cell #1
		PF6000_FW5_FaultCodeList[97]	98	12	Power Cell #1 Failed To Bypass
		PF6000_FW5_FaultCodeList[98]	99	13	One Phase Lost In Power Cell #1
		PF6000_FW5_FaultCodeList[99]	100	14	Two Phases Lost In Power Cell #1
		PF6000_FW5_FaultCodeList[100]	101	15	Bypass Failure (OV) In Power Cell #1
		PF6000_FW5_FaultCodeList[101]	102	17	IGBT Over Current In Power Cell #2
		PF6000_FW5_FaultCodeList[102]	103	18	Capacitor Abnormal In Power Cell #2
		PF6000_FW5_FaultCodeList[103]	104	19	Input Over Voltage In Power Cell #2
		PF6000_FW5_FaultCodeList[104]	105	20	DCBus Undervolt In Power Cell #2 Warn
		PF6000_FW5_FaultCodeList[105]	106	21	Communication Error In Power Cell #2
		PF6000_FW5_FaultCodeList[106]	107	22	No PWM Pulse For IGBT In Power cell #2
		PF6000_FW5_FaultCodeList[107]	108	25	IGBT Failed To Turn On In Power Cell #2
		PF6000_FW5_FaultCodeList[108]	109	26	Power Cell #2 Bypassed
		PF6000_FW5_FaultCodeList[109]	110	27	Over Temperature In Power Cell #2
		PF6000_FW5_FaultCodeList[110]	111	28	Power Cell #2 Failed To Bypass
		PF6000_FW5_FaultCodeList[111]	112	29	One Phase Lost In Power Cell #2
		PF6000_FW5_FaultCodeList[112]	113	30	Two Phases Lost In Power Cell #2
		PF6000_FW5_FaultCodeList[113]	114	31	Bypass Failure (OV) In Power Cell #2
		PF6000_FW5_FaultCodeList[114]	115	33	IGBT Over Current In Power Cell #3
		PF6000_FW5_FaultCodeList[115]	116	34	Capacitor Abnormal In Power Cell #3
		PF6000_FW5_FaultCodeList[116]	117	35	Input Over Voltage In Power Cell #3
		PF6000_FW5_FaultCodeList[117]	118	36	DCBus Undervolt In Power Cell #3 Warn
		PF6000_FW5_FaultCodeList[118]	119	37	Communication Error In Power Cell #3
		PF6000_FW5_FaultCodeList[119]	120	38	No PWM Pulse For IGBT In Power cell #3
		PF6000_FW5_FaultCodeList[120]	121	41	IGBT Failed To Turn On In Power Cell #3
		PF6000_FW5_FaultCodeList[121]	122	42	Power Cell #3 Bypassed
		PF6000_FW5_FaultCodeList[122]	123	43	Over Temperature In Power Cell #3
		PF6000_FW5_FaultCodeList[123]	124	44	Power Cell #3 Failed To Bypass
		PF6000_FW5_FaultCodeList[124]	125	45	One Phase Lost In Power Cell #3
		PF6000_FW5_FaultCodeList[125]	126	46	Two Phases Lost In Power Cell #3
		PF6000_FW5_FaultCodeList[126]	127	47	Bypass Failure (OV) In Power Cell #3
		PF6000_FW5_FaultCodeList[127]	128	49	IGBT Over Current In Power Cell #4
		PF6000_FW5_FaultCodeList[128]	129	50	Capacitor Abnormal In Power Cell #4
		PF6000_FW5_FaultCodeList[129]	130	51	Input Over Voltage In Power Cell #4
		PF6000_FW5_FaultCodeList[130]	131	52	DCBus Undervolt In Power Cell #4 Warn
		PF6000_FW5_FaultCodeList[131]	132	53	Communication Error In Power Cell #4
		PF6000_FW5_FaultCodeList[132]	133	54	No PWM Pulse For IGBT In Power cell #4
		PF6000_FW5_FaultCodeList[133]	134	57	IGBT Failed To Turn On In Power Cell #4
		PF6000_FW5_FaultCodeList[134]	135	58	Power Cell #4 Bypassed
		PF6000_FW5_FaultCodeList[135]	136	59	Over Temperature In Power Cell #4
		PF6000_FW5_FaultCodeList[136]	137	60	Power Cell #4 Failed To Bypass
		PF6000_FW5_FaultCodeList[137]	138	61	One Phase Lost In Power Cell #4
		PF6000_FW5_FaultCodeList[138]	139	62	Two Phases Lost In Power Cell #4
		PF6000_FW5_FaultCodeList[139]	140	63	Bypass Failure (OV) In Power Cell #4
		PF6000_FW5_FaultCodeList[140]	141	65	IGBT Over Current In Power Cell #5
		PF6000_FW5_FaultCodeList[141]	142	66	Capacitor Abnormal In Power Cell #5
		PF6000_FW5_FaultCodeList[142]	143	67	Input Over Voltage In Power Cell #5
		PF6000_FW5_FaultCodeList[143]	144	68	DCBus Undervolt In Power Cell #5 Warn
		PF6000_FW5_FaultCodeList[144]	145	69	Communication Error In Power Cell #5
		PF6000_FW5_FaultCodeList[145]	146	70	No PWM Pulse For IGBT In Power cell #5
		PF6000_FW5_FaultCodeList[146]	147	73	IGBT Failed To Turn On In Power Cell #5
		PF6000_FW5_FaultCodeList[147]	148	74	Power Cell #5 Bypassed
		PF6000_FW5_FaultCodeList[148]	149	75	Over Temperature In Power Cell #5
		PF6000_FW5_FaultCodeList[149]	150	76	Power Cell #5 Failed To Bypass
		PF6000_FW5_FaultCodeList[150]	151	77	One Phase Lost In Power Cell #5
		PF6000_FW5_FaultCodeList[151]	152	78	Two Phases Lost In Power Cell #5
		PF6000_FW5_FaultCodeList[152]	153	79	Bypass Failure (OV) In Power Cell #5
		PF6000_FW5_FaultCodeList[153]	154	81	IGBT Over Current In Power Cell #6
		PF6000_FW5_FaultCodeList[154]	155	82	Capacitor Abnormal In Power Cell #6
		PF6000_FW5_FaultCodeList[155]	156	83	Input Over Voltage In Power Cell #6
		PF6000_FW5_FaultCodeList[156]	157	84	DCBus Undervolt In Power Cell #6 Warn
		PF6000_FW5_FaultCodeList[157]	158	85	Communication Error In Power Cell #6
		PF6000_FW5_FaultCodeList[158]	159	86	No PWM Pulse For IGBT In Power cell #6
		PF6000_FW5_FaultCodeList[159]	160	89	IGBT Failed To Turn On In Power Cell #6
		PF6000_FW5_FaultCodeList[160]	161	90	Power Cell #6 Bypassed
		PF6000_FW5_FaultCodeList[161]	162	91	Over Temperature In Power Cell #6
		PF6000_FW5_FaultCodeList[162]	163	92	Power Cell #6 Failed To Bypass
		PF6000_FW5_FaultCodeList[163]	164	93	One Phase Lost In Power Cell #6
		PF6000_FW5_FaultCodeList[164]	165	94	Two Phases Lost In Power Cell #6
		PF6000_FW5_FaultCodeList[165]	166	95	Bypass Failure (OV) In Power Cell #6
		PF6000_FW5_FaultCodeList[166]	167	97	IGBT Over Current In Power Cell #7
		PF6000_FW5_FaultCodeList[167]	168	98	Capacitor Abnormal In Power Cell #7
		PF6000_FW5_FaultCodeList[168]	169	99	Input Over Voltage In Power Cell #7
		PF6000_FW5_FaultCodeList[169]	170	100	DCBus Undervolt In Power Cell #7 Warn
		PF6000_FW5_FaultCodeList[170]	171	101	Communication Error In Power Cell #7
		PF6000_FW5_FaultCodeList[171]	172	102	No PWM Pulse For IGBT In Power cell #7
		PF6000_FW5_FaultCodeList[172]	173	105	IGBT Failed To Turn On In Power Cell #7
		PF6000_FW5_FaultCodeList[173]	174	106	Power Cell #7 Bypassed
		PF6000_FW5_FaultCodeList[174]	175	107	Over Temperature In Power Cell #7
		PF6000_FW5_FaultCodeList[175]	176	108	Power Cell #7 Failed To Bypass
		PF6000_FW5_FaultCodeList[176]	177	109	One Phase Lost In Power Cell #7
		PF6000_FW5_FaultCodeList[177]	178	110	Two Phases Lost In Power Cell #7
		PF6000_FW5_FaultCodeList[178]	179	111	Bypass Failure (OV) In Power Cell #7
		PF6000_FW5_FaultCodeList[179]	180	113	IGBT Over Current In Power Cell #8
		PF6000_FW5_FaultCodeList[180]	181	114	Capacitor Abnormal In Power Cell #8
		PF6000_FW5_FaultCodeList[181]	182	115	Input Over Voltage In Power Cell #8
		PF6000_FW5_FaultCodeList[182]	183	116	DCBus Undervolt In Power Cell #8 Warn
		PF6000_FW5_FaultCodeList[183]	184	117	Communication Error In Power Cell #8
		PF6000_FW5_FaultCodeList[184]	185	118	No PWM Pulse For IGBT In Power cell #8
		PF6000_FW5_FaultCodeList[185]	186	121	IGBT Failed To Turn On In Power Cell #8
		PF6000_FW5_FaultCodeList[186]	187	122	Power Cell #8 Bypassed
		PF6000_FW5_FaultCodeList[187]	188	123	Over Temperature In Power Cell #8
		PF6000_FW5_FaultCodeList[188]	189	124	Power Cell #8 Failed To Bypass
		PF6000_FW5_FaultCodeList[189]	190	125	One Phase Lost In Power Cell #8
		PF6000_FW5_FaultCodeList[190]	191	126	Two Phases Lost In Power Cell #8
		PF6000_FW5_FaultCodeList[191]	192	127	Bypass Failure (OV) In Power Cell #8
		PF6000_FW5_FaultCodeList[192]	193	129	IGBT Over Current In Power Cell #9
		PF6000_FW5_FaultCodeList[193]	194	130	Capacitor Abnormal In Power Cell #9
		PF6000_FW5_FaultCodeList[194]	195	131	Input Over Voltage In Power Cell #9
		PF6000_FW5_FaultCodeList[195]	196	132	DCBus Undervolt In Power Cell #9 Warn
		PF6000_FW5_FaultCodeList[196]	197	133	Communication Error In Power Cell #9
		PF6000_FW5_FaultCodeList[197]	198	134	No PWM Pulse For IGBT In Power cell #9
		PF6000_FW5_FaultCodeList[198]	199	137	IGBT Failed To Turn On In Power Cell #9
		PF6000_FW5_FaultCodeList[199]	200	138	Power Cell #9 Bypassed
		PF6000_FW5_FaultCodeList[200]	201	139	Over Temperature In Power Cell #9
		PF6000_FW5_FaultCodeList[201]	202	140	Power Cell #9 Failed To Bypass
		PF6000_FW5_FaultCodeList[202]	203	141	One Phase Lost In Power Cell #9
		PF6000_FW5_FaultCodeList[203]	204	142	Two Phases Lost In Power Cell #9
		PF6000_FW5_FaultCodeList[204]	205	143	Bypass Failure (OV) In Power Cell #9
		PF6000_FW5_FaultCodeList[205]	206	145	IGBT Over Current In Power Cell #10
		PF6000_FW5_FaultCodeList[206]	207	146	Capacitor Abnormal In Power Cell #10
		PF6000_FW5_FaultCodeList[207]	208	147	Input Over Voltage In Power Cell #10
		PF6000_FW5_FaultCodeList[208]	209	148	DCBus Undervolt In Power Cell #10 Warn
		PF6000_FW5_FaultCodeList[209]	210	149	Communication Error In Power Cell #10
		PF6000_FW5_FaultCodeList[210]	211	150	No PWM Pulse For IGBT In Power cell #10
		PF6000_FW5_FaultCodeList[211]	212	153	IGBT Failed To Turn On In Power Cell #10
		PF6000_FW5_FaultCodeList[212]	213	154	Power Cell #10 Bypassed
		PF6000_FW5_FaultCodeList[213]	214	155	Over Temperature In Power Cell #10
		PF6000_FW5_FaultCodeList[214]	215	156	Power Cell #10 Failed To Bypass
		PF6000_FW5_FaultCodeList[215]	216	157	One Phase Lost In Power Cell #10
		PF6000_FW5_FaultCodeList[216]	217	158	Two Phases Lost In Power Cell #10
		PF6000_FW5_FaultCodeList[217]	218	159	Bypass Failure (OV) In Power Cell #10
		PF6000_FW5_FaultCodeList[218]	219	161	IGBT Over Current In Power Cell #11
		PF6000_FW5_FaultCodeList[219]	220	162	Capacitor Abnormal In Power Cell #11
		PF6000_FW5_FaultCodeList[220]	221	163	Input Over Voltage In Power Cell #11
		PF6000_FW5_FaultCodeList[221]	222	164	DCBus Undervolt In Power Cell #11 Warn
		PF6000_FW5_FaultCodeList[222]	223	165	Communication Error In Power Cell #11
		PF6000_FW5_FaultCodeList[223]	224	166	No PWM Pulse For IGBT In Power cell #11
		PF6000_FW5_FaultCodeList[224]	225	169	IGBT Failed To Turn On In Power Cell #11
		PF6000_FW5_FaultCodeList[225]	226	170	Power Cell #11 Bypassed
		PF6000_FW5_FaultCodeList[226]	227	171	Over Temperature In Power Cell #11
		PF6000_FW5_FaultCodeList[227]	228	172	Power Cell #11 Failed To Bypass
		PF6000_FW5_FaultCodeList[228]	229	173	One Phase Lost In Power Cell #11
		PF6000_FW5_FaultCodeList[229]	230	174	Two Phases Lost In Power Cell #11
		PF6000_FW5_FaultCodeList[230]	231	175	Bypass Failure (OV) In Power Cell #11
		PF6000_FW5_FaultCodeList[231]	232	177	IGBT Over Current In Power Cell #12
		PF6000_FW5_FaultCodeList[232]	233	178	Capacitor Abnormal In Power Cell #12
		PF6000_FW5_FaultCodeList[233]	234	179	Input Over Voltage In Power Cell #12
		PF6000_FW5_FaultCodeList[234]	235	180	DCBus Undervolt In Power Cell #12 Warn
		PF6000_FW5_FaultCodeList[235]	236	181	Communication Error In Power Cell #12
		PF6000_FW5_FaultCodeList[236]	237	182	No PWM Pulse For IGBT In Power cell #12
		PF6000_FW5_FaultCodeList[237]	238	185	IGBT Failed To Turn On In Power Cell #12
		PF6000_FW5_FaultCodeList[238]	239	186	Power Cell #12 Bypassed
		PF6000_FW5_FaultCodeList[239]	240	187	Over Temperature In Power Cell #12
		PF6000_FW5_FaultCodeList[240]	241	188	Power Cell #12 Failed To Bypass
		PF6000_FW5_FaultCodeList[241]	242	189	One Phase Lost In Power Cell #12
		PF6000_FW5_FaultCodeList[242]	243	190	Two Phases Lost In Power Cell #12
		PF6000_FW5_FaultCodeList[243]	244	191	Bypass Failure (OV) In Power Cell #12
		PF6000_FW5_FaultCodeList[244]	245	193	IGBT Over Current In Power Cell #13
		PF6000_FW5_FaultCodeList[245]	246	194	Capacitor Abnormal In Power Cell #13
		PF6000_FW5_FaultCodeList[246]	247	195	Input Over Voltage In Power Cell #13
		PF6000_FW5_FaultCodeList[247]	248	196	DCBus Undervolt In Power Cell #13 Warn
		PF6000_FW5_FaultCodeList[248]	249	197	Communication Error In Power Cell #13
		PF6000_FW5_FaultCodeList[249]	250	198	No PWM Pulse For IGBT In Power cell #13
		PF6000_FW5_FaultCodeList[250]	251	201	IGBT Failed To Turn On In Power Cell #13
		PF6000_FW5_FaultCodeList[251]	252	202	Power Cell #13 Bypassed
		PF6000_FW5_FaultCodeList[252]	253	203	Over Temperature In Power Cell #13
		PF6000_FW5_FaultCodeList[253]	254	204	Power Cell #13 Failed To Bypass
		PF6000_FW5_FaultCodeList[254]	255	205	One Phase Lost In Power Cell #13
		PF6000_FW5_FaultCodeList[255]	256	206	Two Phases Lost In Power Cell #13
		PF6000_FW5_FaultCodeList[256]	257	207	Bypass Failure (OV) In Power Cell #13
		PF6000_FW5_FaultCodeList[257]	258	209	IGBT Over Current In Power Cell #14
		PF6000_FW5_FaultCodeList[258]	259	210	Capacitor Abnormal In Power Cell #14
		PF6000_FW5_FaultCodeList[259]	260	211	Input Over Voltage In Power Cell #14
		PF6000_FW5_FaultCodeList[260]	261	212	DCBus Undervolt In Power Cell #14 Warn
		PF6000_FW5_FaultCodeList[261]	262	213	Communication Error In Power Cell #14
		PF6000_FW5_FaultCodeList[262]	263	214	No PWM Pulse For IGBT In Power cell #14
		PF6000_FW5_FaultCodeList[263]	264	217	IGBT Failed To Turn On In Power Cell #14
		PF6000_FW5_FaultCodeList[264]	265	218	Power Cell #14 Bypassed
		PF6000_FW5_FaultCodeList[265]	266	219	Over Temperature In Power Cell #14
		PF6000_FW5_FaultCodeList[266]	267	220	Power Cell #14 Failed To Bypass
		PF6000_FW5_FaultCodeList[267]	268	221	One Phase Lost In Power Cell #14
		PF6000_FW5_FaultCodeList[268]	269	222	Two Phases Lost In Power Cell #14
		PF6000_FW5_FaultCodeList[269]	270	223	Bypass Failure (OV) In Power Cell #14
		PF6000_FW5_FaultCodeList[270]	271	225	IGBT Over Current In Power Cell #15
		PF6000_FW5_FaultCodeList[271]	272	226	Capacitor Abnormal In Power Cell #15
		PF6000_FW5_FaultCodeList[272]	273	227	Input Over Voltage In Power Cell #15
		PF6000_FW5_FaultCodeList[273]	274	228	DCBus Undervolt In Power Cell #15 Warn
		PF6000_FW5_FaultCodeList[274]	275	229	Communication Error In Power Cell #15
		PF6000_FW5_FaultCodeList[275]	276	230	No PWM Pulse For IGBT In Power cell #15
		PF6000_FW5_FaultCodeList[276]	277	233	IGBT Failed To Turn On In Power Cell #15
		PF6000_FW5_FaultCodeList[277]	278	234	Power Cell #15 Bypassed
		PF6000_FW5_FaultCodeList[278]	279	235	Over Temperature In Power Cell #15
		PF6000_FW5_FaultCodeList[279]	280	236	Power Cell #15 Failed To Bypass
		PF6000_FW5_FaultCodeList[280]	281	237	One Phase Lost In Power Cell #15
		PF6000_FW5_FaultCodeList[281]	282	238	Two Phases Lost In Power Cell #15
		PF6000_FW5_FaultCodeList[282]	283	239	Bypass Failure (OV) In Power Cell #15
		PF6000_FW5_FaultCodeList[283]	284	241	IGBT Over Current In Power Cell #16
		PF6000_FW5_FaultCodeList[284]	285	242	Capacitor Abnormal In Power Cell #16
		PF6000_FW5_FaultCodeList[285]	286	243	Input Over Voltage In Power Cell #16
		PF6000_FW5_FaultCodeList[286]	287	244	DCBus Undervolt In Power Cell #16 Warn
		PF6000_FW5_FaultCodeList[287]	288	245	Communication Error In Power Cell #16
		PF6000_FW5_FaultCodeList[288]	289	246	No PWM Pulse For IGBT In Power cell #16
		PF6000_FW5_FaultCodeList[289]	290	249	IGBT Failed To Turn On In Power Cell #16
		PF6000_FW5_FaultCodeList[290]	291	250	Power Cell #16 Bypassed
		PF6000_FW5_FaultCodeList[291]	292	251	Over Temperature In Power Cell #16
		PF6000_FW5_FaultCodeList[292]	293	252	Power Cell #16 Failed To Bypass
		PF6000_FW5_FaultCodeList[293]	294	253	One Phase Lost In Power Cell #16
		PF6000_FW5_FaultCodeList[294]	295	254	Two Phases Lost In Power Cell #16
		PF6000_FW5_FaultCodeList[295]	296	255	Bypass Failure (OV) In Power Cell #16
		PF6000_FW5_FaultCodeList[296]	297	257	IGBT Over Current In Power Cell #17
		PF6000_FW5_FaultCodeList[297]	298	258	Capacitor Abnormal In Power Cell #17
		PF6000_FW5_FaultCodeList[298]	299	259	Input Over Voltage In Power Cell #17
		PF6000_FW5_FaultCodeList[299]	300	260	DCBus Undervolt In Power Cell #17 Warn
		PF6000_FW5_FaultCodeList[300]	301	261	Communication Error In Power Cell #17
		PF6000_FW5_FaultCodeList[301]	302	262	No PWM Pulse For IGBT In Power cell #17
		PF6000_FW5_FaultCodeList[302]	303	265	IGBT Failed To Turn On In Power Cell #17
		PF6000_FW5_FaultCodeList[303]	304	266	Power Cell #17 Bypassed
		PF6000_FW5_FaultCodeList[304]	305	267	Over Temperature In Power Cell #17
		PF6000_FW5_FaultCodeList[305]	306	268	Power Cell #17 Failed To Bypass
		PF6000_FW5_FaultCodeList[306]	307	269	One Phase Lost In Power Cell #17
		PF6000_FW5_FaultCodeList[307]	308	270	Two Phases Lost In Power Cell #17
		PF6000_FW5_FaultCodeList[308]	309	271	Bypass Failure (OV) In Power Cell #17
		PF6000_FW5_FaultCodeList[309]	310	273	IGBT Over Current In Power Cell #18
		PF6000_FW5_FaultCodeList[310]	311	274	Capacitor Abnormal In Power Cell #18
		PF6000_FW5_FaultCodeList[311]	312	275	Input Over Voltage In Power Cell #18
		PF6000_FW5_FaultCodeList[312]	313	276	DCBus Undervolt In Power Cell #18 Warn
		PF6000_FW5_FaultCodeList[313]	314	277	Communication Error In Power Cell #18
		PF6000_FW5_FaultCodeList[314]	315	278	No PWM Pulse For IGBT In Power cell #18
		PF6000_FW5_FaultCodeList[315]	316	281	IGBT Failed To Turn On In Power Cell #18
		PF6000_FW5_FaultCodeList[316]	317	282	Power Cell #18 Bypassed
		PF6000_FW5_FaultCodeList[317]	318	283	Over Temperature In Power Cell #18
		PF6000_FW5_FaultCodeList[318]	319	284	Power Cell #18 Failed To Bypass
		PF6000_FW5_FaultCodeList[319]	320	285	One Phase Lost In Power Cell #18
		PF6000_FW5_FaultCodeList[320]	321	286	Two Phases Lost In Power Cell #18
		PF6000_FW5_FaultCodeList[321]	322	287	Bypass Failure (OV) In Power Cell #18
		PF6000_FW5_FaultCodeList[322]	323	289	IGBT Over Current In Power Cell #19
		PF6000_FW5_FaultCodeList[323]	324	290	Capacitor Abnormal In Power Cell #19
		PF6000_FW5_FaultCodeList[324]	325	291	Input Over Voltage In Power Cell #19
		PF6000_FW5_FaultCodeList[325]	326	292	DCBus Undervolt In Power Cell #19 Warn
		PF6000_FW5_FaultCodeList[326]	327	293	Communication Error In Power Cell #19
		PF6000_FW5_FaultCodeList[327]	328	294	No PWM Pulse For IGBT In Power cell #19
		PF6000_FW5_FaultCodeList[328]	329	297	IGBT Failed To Turn On In Power Cell #19
		PF6000_FW5_FaultCodeList[329]	330	298	Power Cell #19 Bypassed
		PF6000_FW5_FaultCodeList[330]	331	299	Over Temperature In Power Cell #19
		PF6000_FW5_FaultCodeList[331]	332	300	Power Cell #19 Failed To Bypass
		PF6000_FW5_FaultCodeList[332]	333	301	One Phase Lost In Power Cell #19
		PF6000_FW5_FaultCodeList[333]	334	302	Two Phases Lost In Power Cell #19
		PF6000_FW5_FaultCodeList[334]	335	303	Bypass Failure (OV) In Power Cell #19
		PF6000_FW5_FaultCodeList[335]	336	305	IGBT Over Current In Power Cell #20
		PF6000_FW5_FaultCodeList[336]	337	306	Capacitor Abnormal In Power Cell #20
		PF6000_FW5_FaultCodeList[337]	338	307	Input Over Voltage In Power Cell #20
		PF6000_FW5_FaultCodeList[338]	339	308	DCBus Undervolt In Power Cell #20 Warn
		PF6000_FW5_FaultCodeList[339]	340	309	Communication Error In Power Cell #20
		PF6000_FW5_FaultCodeList[340]	341	310	No PWM Pulse For IGBT In Power cell #20
		PF6000_FW5_FaultCodeList[341]	342	313	IGBT Failed To Turn On In Power Cell #20
		PF6000_FW5_FaultCodeList[342]	343	314	Power Cell #20 Bypassed
		PF6000_FW5_FaultCodeList[343]	344	315	Over Temperature In Power Cell #20
		PF6000_FW5_FaultCodeList[344]	345	316	Power Cell #20 Failed To Bypass
		PF6000_FW5_FaultCodeList[345]	346	317	One Phase Lost In Power Cell #20
		PF6000_FW5_FaultCodeList[346]	347	318	Two Phases Lost In Power Cell #20
		PF6000_FW5_FaultCodeList[347]	348	319	Bypass Failure (OV) In Power Cell #20
		PF6000_FW5_FaultCodeList[348]	349	321	IGBT Over Current In Power Cell #21
		PF6000_FW5_FaultCodeList[349]	350	322	Capacitor Abnormal In Power Cell #21
		PF6000_FW5_FaultCodeList[350]	351	323	Input Over Voltage In Power Cell #21
		PF6000_FW5_FaultCodeList[351]	352	324	DCBus Undervolt In Power Cell #21 Warn
		PF6000_FW5_FaultCodeList[352]	353	325	Communication Error In Power Cell #21
		PF6000_FW5_FaultCodeList[353]	354	326	No PWM Pulse For IGBT In Power cell #21
		PF6000_FW5_FaultCodeList[354]	355	329	IGBT Failed To Turn On In Power Cell #21
		PF6000_FW5_FaultCodeList[355]	356	330	Power Cell #21 Bypassed
		PF6000_FW5_FaultCodeList[356]	357	331	Over Temperature In Power Cell #21
		PF6000_FW5_FaultCodeList[357]	358	332	Power Cell #21 Failed To Bypass
		PF6000_FW5_FaultCodeList[358]	359	333	One Phase Lost In Power Cell #21
		PF6000_FW5_FaultCodeList[359]	360	334	Two Phases Lost In Power Cell #21
		PF6000_FW5_FaultCodeList[360]	361	335	Bypass Failure (OV) In Power Cell #21
		PF6000_FW5_FaultCodeList[361]	362	337	IGBT Over Current In Power Cell #22
		PF6000_FW5_FaultCodeList[362]	363	338	Capacitor Abnormal In Power Cell #22
		PF6000_FW5_FaultCodeList[363]	364	339	Input Over Voltage In Power Cell #22
		PF6000_FW5_FaultCodeList[364]	365	340	DCBus Undervolt In Power Cell #22 Warn
		PF6000_FW5_FaultCodeList[365]	366	341	Communication Error In Power Cell #22
		PF6000_FW5_FaultCodeList[366]	367	342	No PWM Pulse For IGBT In Power cell #22
		PF6000_FW5_FaultCodeList[367]	368	345	IGBT Failed To Turn On In Power Cell #22
		PF6000_FW5_FaultCodeList[368]	369	346	Power Cell #22 Bypassed
		PF6000_FW5_FaultCodeList[369]	370	347	Over Temperature In Power Cell #22
		PF6000_FW5_FaultCodeList[370]	371	348	Power Cell #22 Failed To Bypass
		PF6000_FW5_FaultCodeList[371]	372	349	One Phase Lost In Power Cell #22
		PF6000_FW5_FaultCodeList[372]	373	350	Two Phases Lost In Power Cell #22
		PF6000_FW5_FaultCodeList[373]	374	351	Bypass Failure (OV) In Power Cell #22
		PF6000_FW5_FaultCodeList[374]	375	353	IGBT Over Current In Power Cell #23
		PF6000_FW5_FaultCodeList[375]	376	354	Capacitor Abnormal In Power Cell #23
		PF6000_FW5_FaultCodeList[376]	377	355	Input Over Voltage In Power Cell #23
		PF6000_FW5_FaultCodeList[377]	378	356	DCBus Undervolt In Power Cell #23 Warn
		PF6000_FW5_FaultCodeList[378]	379	357	Communication Error In Power Cell #23
		PF6000_FW5_FaultCodeList[379]	380	358	No PWM Pulse For IGBT In Power cell #23
		PF6000_FW5_FaultCodeList[380]	381	361	IGBT Failed To Turn On In Power Cell #23
		PF6000_FW5_FaultCodeList[381]	382	362	Power Cell #23 Bypassed
		PF6000_FW5_FaultCodeList[382]	383	363	Over Temperature In Power Cell #23
		PF6000_FW5_FaultCodeList[383]	384	364	Power Cell #23 Failed To Bypass
		PF6000_FW5_FaultCodeList[384]	385	365	One Phase Lost In Power Cell #23
		PF6000_FW5_FaultCodeList[385]	386	366	Two Phases Lost In Power Cell #23
		PF6000_FW5_FaultCodeList[386]	387	367	Bypass Failure (OV) In Power Cell #23
		PF6000_FW5_FaultCodeList[387]	388	369	IGBT Over Current In Power Cell #24
		PF6000_FW5_FaultCodeList[388]	389	370	Capacitor Abnormal In Power Cell #24
		PF6000_FW5_FaultCodeList[389]	390	371	Input Over Voltage In Power Cell #24
		PF6000_FW5_FaultCodeList[390]	391	372	DCBus Undervolt In Power Cell #24 Warn
		PF6000_FW5_FaultCodeList[391]	392	373	Communication Error In Power Cell #24
		PF6000_FW5_FaultCodeList[392]	393	374	No PWM Pulse For IGBT In Power cell #24
		PF6000_FW5_FaultCodeList[393]	394	377	IGBT Failed To Turn On In Power Cell #24
		PF6000_FW5_FaultCodeList[394]	395	378	Power Cell #24 Bypassed
		PF6000_FW5_FaultCodeList[395]	396	379	Over Temperature In Power Cell #24
		PF6000_FW5_FaultCodeList[396]	397	380	Power Cell #24 Failed To Bypass
		PF6000_FW5_FaultCodeList[397]	398	381	One Phase Lost In Power Cell #24
		PF6000_FW5_FaultCodeList[398]	399	382	Two Phases Lost In Power Cell #24
		PF6000_FW5_FaultCodeList[399]	400	383	Bypass Failure (OV) In Power Cell #24
		PF6000_FW5_FaultCodeList[400]	401	385	IGBT Over Current In Power Cell #25
		PF6000_FW5_FaultCodeList[401]	402	386	Capacitor Abnormal In Power Cell #25
		PF6000_FW5_FaultCodeList[402]	403	387	Input Over Voltage In Power Cell #25
		PF6000_FW5_FaultCodeList[403]	404	388	DCBus Undervolt In Power Cell #25 Warn
		PF6000_FW5_FaultCodeList[404]	405	389	Communication Error In Power Cell #25
		PF6000_FW5_FaultCodeList[405]	406	390	No PWM Pulse For IGBT In Power cell #25
		PF6000_FW5_FaultCodeList[406]	407	393	IGBT Failed To Turn On In Power Cell #25
		PF6000_FW5_FaultCodeList[407]	408	394	Power Cell #25 Bypassed
		PF6000_FW5_FaultCodeList[408]	409	395	Over Temperature In Power Cell #25
		PF6000_FW5_FaultCodeList[409]	410	396	Power Cell #25 Failed To Bypass
		PF6000_FW5_FaultCodeList[410]	411	397	One Phase Lost In Power Cell #25
		PF6000_FW5_FaultCodeList[411]	412	398	Two Phases Lost In Power Cell #25
		PF6000_FW5_FaultCodeList[412]	413	399	Bypass Failure (OV) In Power Cell #25
		PF6000_FW5_FaultCodeList[413]	414	401	IGBT Over Current In Power Cell #26
		PF6000_FW5_FaultCodeList[414]	415	402	Capacitor Abnormal In Power Cell #26
		PF6000_FW5_FaultCodeList[415]	416	403	Input Over Voltage In Power Cell #26
		PF6000_FW5_FaultCodeList[416]	417	404	DCBus Undervolt In Power Cell #26 Warn
		PF6000_FW5_FaultCodeList[417]	418	405	Communication Error In Power Cell #26
		PF6000_FW5_FaultCodeList[418]	419	406	No PWM Pulse For IGBT In Power cell #26
		PF6000_FW5_FaultCodeList[419]	420	409	IGBT Failed To Turn On In Power Cell #26
		PF6000_FW5_FaultCodeList[420]	421	410	Power Cell #26 Bypassed
		PF6000_FW5_FaultCodeList[421]	422	411	Over Temperature In Power Cell #26
		PF6000_FW5_FaultCodeList[422]	423	412	Power Cell #26 Failed To Bypass
		PF6000_FW5_FaultCodeList[423]	424	413	One Phase Lost In Power Cell #26
		PF6000_FW5_FaultCodeList[424]	425	414	Two Phases Lost In Power Cell #26
		PF6000_FW5_FaultCodeList[425]	426	415	Bypass Failure (OV) In Power Cell #26
		PF6000_FW5_FaultCodeList[426]	427	417	IGBT Over Current In Power Cell #27
		PF6000_FW5_FaultCodeList[427]	428	418	Capacitor Abnormal In Power Cell #27
		PF6000_FW5_FaultCodeList[428]	429	419	Input Over Voltage In Power Cell #27
		PF6000_FW5_FaultCodeList[429]	430	420	DCBus Undervolt In Power Cell #27 Warn
		PF6000_FW5_FaultCodeList[430]	431	421	Communication Error In Power Cell #27
		PF6000_FW5_FaultCodeList[431]	432	422	No PWM Pulse For IGBT In Power cell #27
		PF6000_FW5_FaultCodeList[432]	433	425	IGBT Failed To Turn On In Power Cell #27
		PF6000_FW5_FaultCodeList[433]	434	426	Power Cell #27 Bypassed
		PF6000_FW5_FaultCodeList[434]	435	427	Over Temperature In Power Cell #27
		PF6000_FW5_FaultCodeList[435]	436	428	Power Cell #27 Failed To Bypass
		PF6000_FW5_FaultCodeList[436]	437	429	One Phase Lost In Power Cell #27
		PF6000_FW5_FaultCodeList[437]	438	430	Two Phases Lost In Power Cell #27
		PF6000_FW5_FaultCodeList[438]	439	431	Bypass Failure (OV) In Power Cell #27
		PF6000_FW5_FaultCodeList[439]	440	497	PWMA Board Incompatible With PUA1 Board
		PF6000_FW5_FaultCodeList[440]	441	498	PWMA Board Incompatible With PUA2 Board
		PF6000_FW5_FaultCodeList[441]	442	499	PWMA Board Incompatible With PUA3 Board
		PF6000_FW5_FaultCodeList[442]	443	500	PWMA Board Incompatible With PUA4 Board
		PF6000_FW5_FaultCodeList[443]	444	501	PWMA Board Incompatible With PUA5 Board
		PF6000_FW5_FaultCodeList[444]	445	502	PWMA Board Incompatible With PUA6 Board
		PF6000_FW5_FaultCodeList[445]	446	503	PWMA Board Incompatible With PUA7 Board
		PF6000_FW5_FaultCodeList[446]	447	504	PWMA Board Incompatible With PUA8 Board
		PF6000_FW5_FaultCodeList[447]	448	505	PWMA Board Incompatible With PUA9 Board
		PF6000_FW5_FaultCodeList[448]	449	506	PWMA Board Incompatible With PUA10 Board
		PF6000_FW5_FaultCodeList[449]	450	507	PWMA Board Incompatible With PUA11 Board
		PF6000_FW5_FaultCodeList[450]	451	508	PWMA Board Incompatible With PUA12 Board
		PF6000_FW5_FaultCodeList[451]	452	509	PWMA Board Incompatible With PUA13 Board
		PF6000_FW5_FaultCodeList[452]	453	510	Pri. FPGA Incompatible With PWMA Board
		PF6000_FW5_FaultCodeList[453]	454	511	Pri. FPGA Incompatible With PWMB Board
		PF6000_FW5_FaultCodeList[454]	455	512	Pri. FPGA Incompatible With PWMC Board
		PF6000_FW5_FaultCodeList[455]	456	513	PWMB Board Incompatible With PUB1 Board
		PF6000_FW5_FaultCodeList[456]	457	514	PWMB Board Incompatible With PUB2 Board
		PF6000_FW5_FaultCodeList[457]	458	515	PWMB Board Incompatible With PUB3 Board
		PF6000_FW5_FaultCodeList[458]	459	516	PWMB Board Incompatible With PUB4 Board
		PF6000_FW5_FaultCodeList[459]	460	517	PWMB Board Incompatible With PUB5 Board
		PF6000_FW5_FaultCodeList[460]	461	518	PWMB Board Incompatible With PUB6 Board
		PF6000_FW5_FaultCodeList[461]	462	519	PWMB Board Incompatible With PUB7 Board
		PF6000_FW5_FaultCodeList[462]	463	520	PWMB Board Incompatible With PUB8 Board
		PF6000_FW5_FaultCodeList[463]	464	521	PWMB Board Incompatible With PUB9 Board
		PF6000_FW5_FaultCodeList[464]	465	522	PWMB Board Incompatible With PUB10 Board
		PF6000_FW5_FaultCodeList[465]	466	523	PWMB Board Incompatible With PUB11 Board
		PF6000_FW5_FaultCodeList[466]	467	524	PWMB Board Incompatible With PUB12 Board
		PF6000_FW5_FaultCodeList[467]	468	525	PWMB Board Incompatible With PUB13 Board
		PF6000_FW5_FaultCodeList[468]	469	526	Pri. FPGA Incompatible With DT Board
		PF6000_FW5_FaultCodeList[469]	470	527	Pri. DSP Incompatible With Pri. FPGA
		PF6000_FW5_FaultCodeList[470]	471	528	Pri. DSP Incompatible With Secondary DSP
		PF6000_FW5_FaultCodeList[471]	472	529	PWMC Board Incompatible With PUC1 Board
		PF6000_FW5_FaultCodeList[472]	473	530	PWMC Board Incompatible With PUC2 Board
		PF6000_FW5_FaultCodeList[473]	474	531	PWMC Board Incompatible With PUC3 Board
		PF6000_FW5_FaultCodeList[474]	475	532	PWMC Board Incompatible With PUC4 Board
		PF6000_FW5_FaultCodeList[475]	476	533	PWMC Board Incompatible With PUC5 Board
		PF6000_FW5_FaultCodeList[476]	477	534	PWMC Board Incompatible With PUC6 Board
		PF6000_FW5_FaultCodeList[477]	478	535	PWMC Board Incompatible With PUC7 Board
		PF6000_FW5_FaultCodeList[478]	479	536	PWMC Board Incompatible With PUC8 Board
		PF6000_FW5_FaultCodeList[479]	480	537	PWMC Board Incompatible With PUC9 Board
		PF6000_FW5_FaultCodeList[480]	481	538	PWMC Board Incompatible With PUC10 Board
		PF6000_FW5_FaultCodeList[481]	482	539	PWMC Board Incompatible With PUC11 Board
		PF6000_FW5_FaultCodeList[482]	483	540	PWMC Board Incompatible With PUC12 Board
		PF6000_FW5_FaultCodeList[483]	484	541	PWMC Board Incompatible With PUC13 Board
		PF6000_FW5_FaultCodeList[484]	485	542	Versions Of System Incompatible
		PF6000_FW5_FaultCodeList[485]	486	543	Version Fault Identification Code Error
		PF6000_FW5_FaultCodeList[486]	487	545	Pri. DSP Incompatible With PLC
		PF6000_FW5_FaultCodeList[487]	488	546	HMI Incompatible With PLC
		PF6000_FW5_FaultCodeList[488]	489	547	Pri. DSP Incompatible With HMI

## PF6000_FW6
	PF6000_FW6_FaultCodeList	Read From CLX:
		Send To CLX:
	Fault codes and text for
	PowerFlex 6000 series MV drives	Description:		Fault Code	Description for given Fault Code
		Usage:		UDT	UDT
		Data Type:		DINT	STRING_40
			(Origin)	.	.
Unit	Tag Description	TagName	Instance	Code	Desc
		Default Values:	0	0	Check drive manual for this fault code
		PF6000_FW6_FaultCodeList[0]	1	0	Check drive manual for this fault code
		PF6000_FW6_FaultCodeList[1]	2	-1	No more fault information found
		PF6000_FW6_FaultCodeList[2]	3	654	DCS Communication Error
		PF6000_FW6_FaultCodeList[3]	4	655	DCS Communication Error Warning
		PF6000_FW6_FaultCodeList[4]	5		Analog Feedback Loss Warning
		PF6000_FW6_FaultCodeList[5]	6	657	Motor Over Temperature
		PF6000_FW6_FaultCodeList[6]	7	658	Filter Cabinet Over Temperature
		PF6000_FW6_FaultCodeList[7]	8	659	Motor Side HECS Power Supply Fault
		PF6000_FW6_FaultCodeList[8]	9	660	Analog Channel #2 Loss Warning
		PF6000_FW6_FaultCodeList[9]	10	433	Motor Over Current 2
		PF6000_FW6_FaultCodeList[10]	11	434	Motor Over Current 1
		PF6000_FW6_FaultCodeList[11]	12	435	Fan Failure In Fan Group #1
		PF6000_FW6_FaultCodeList[12]	13	436	Output Over Voltage
		PF6000_FW6_FaultCodeList[13]	14	437	Abnormal Output Voltage
		PF6000_FW6_FaultCodeList[14]	15	438	Ground Fault
		PF6000_FW6_FaultCodeList[15]	16	439	Over Speed Fault
		PF6000_FW6_FaultCodeList[16]	17	440	Motor Stalled
		PF6000_FW6_FaultCodeList[17]	18	442	Output Phase Over Current
		PF6000_FW6_FaultCodeList[18]	19	443	VFD Over Current 1
		PF6000_FW6_FaultCodeList[19]	20	444	Fan Failure In Fan Group #2
		PF6000_FW6_FaultCodeList[20]	21	445	Pre-Charge Contactor Failure
		PF6000_FW6_FaultCodeList[21]	22	446	Pre-Charge Timeout
		PF6000_FW6_FaultCodeList[22]	23	447	Pre-Charge Repeat Interval Low
		PF6000_FW6_FaultCodeList[23]	24	449	Fan Failure Warning In Fan Group #1
		PF6000_FW6_FaultCodeList[24]	25	450	Abnormal Output Voltage Warning
		PF6000_FW6_FaultCodeList[25]	26	451	Ground Fault Warning
		PF6000_FW6_FaultCodeList[26]	27	452	Output Frequency Deviation Warning
		PF6000_FW6_FaultCodeList[27]	28	454	Input Power Loss, Waiting For Recovery
		PF6000_FW6_FaultCodeList[28]	29	455	Input Voltage Sag, Derating Operating
		PF6000_FW6_FaultCodeList[29]	30	456	Low Voltage Ride Through Operating
		PF6000_FW6_FaultCodeList[30]	31	457	Input Voltage Sag, Flux Controlling
		PF6000_FW6_FaultCodeList[31]	32	458	Fan Failure Warning In Fan Group #2
		PF6000_FW6_FaultCodeList[32]	33	459	Bypass Operating
		PF6000_FW6_FaultCodeList[33]	34	460	DC Bus Under Voltage Warning
		PF6000_FW6_FaultCodeList[34]	35	461	Fan Failure Warning In Fan Group #3
		PF6000_FW6_FaultCodeList[35]	36	462	Line Neutral Over Voltage Warning
		PF6000_FW6_FaultCodeList[36]	37	463	Line Under Voltage Warning
		PF6000_FW6_FaultCodeList[37]	38	464	Fan Failure Warning In Fan Group #4
		PF6000_FW6_FaultCodeList[38]	39	465	Cabinet Door Open While Drive Energized
		PF6000_FW6_FaultCodeList[39]	40	466	E-Stop Trip
		PF6000_FW6_FaultCodeList[40]	41	467	Input Circuit Breaker Tripped
		PF6000_FW6_FaultCodeList[41]	42	468	Non-Zero Frequency Command On Start
		PF6000_FW6_FaultCodeList[42]	43	469	Flying Start Failed
		PF6000_FW6_FaultCodeList[43]	44	474	System Locked
		PF6000_FW6_FaultCodeList[44]	45	475	CPU Board In Wrong Position
		PF6000_FW6_FaultCodeList[45]	46	476	AT Board In Wrong Position
		PF6000_FW6_FaultCodeList[46]	47	477	5V Power Supply Fault
		PF6000_FW6_FaultCodeList[47]	48	478	15V Power Supply Fault
		PF6000_FW6_FaultCodeList[48]	49	479	24V DCS Power Supply Fault
		PF6000_FW6_FaultCodeList[49]	50	480	24V PLC Power Supply Fault
		PF6000_FW6_FaultCodeList[50]	51	481	PWMA Board In Wrong Position
		PF6000_FW6_FaultCodeList[51]	52	482	PWMB Board In Wrong Position
		PF6000_FW6_FaultCodeList[52]	53	483	PWMC Board In Wrong Position
		PF6000_FW6_FaultCodeList[53]	54	484	DT Board In Wrong Position
		PF6000_FW6_FaultCodeList[54]	55	486	Low Voltage Ride Through Over Max Time
		PF6000_FW6_FaultCodeList[55]	56	487	Low Voltage Ride Through Short Interval
		PF6000_FW6_FaultCodeList[56]	57	488	Low Voltage Ride Through Failure
		PF6000_FW6_FaultCodeList[57]	58	489	Input Voltage Loss While Stop
		PF6000_FW6_FaultCodeList[58]	59	490	Input Voltage Loss Over Time Limit
		PF6000_FW6_FaultCodeList[59]	60	492	Input Voltage Loss
		PF6000_FW6_FaultCodeList[60]	61	493	Cell Bypass Timeout
		PF6000_FW6_FaultCodeList[61]	62	494	Cell Bypass Start Fault
		PF6000_FW6_FaultCodeList[62]	63	495	Cell Bypass Logic Fault
		PF6000_FW6_FaultCodeList[63]	64	593	DIP Configuration Fault In PWMA
		PF6000_FW6_FaultCodeList[64]	65	594	Bypass Cell Re-activation Fault
		PF6000_FW6_FaultCodeList[65]	66	595	PCCB Parameters R/W Timeout
		PF6000_FW6_FaultCodeList[66]	67	596	Power Cells Parameters Mismatch
		PF6000_FW6_FaultCodeList[67]	68	597	DC Bus Voltage Deviation Fault
		PF6000_FW6_FaultCodeList[68]	69	598	DIP Configuration Fault In PWMB
		PF6000_FW6_FaultCodeList[69]	70	599	DIP Configuration Fault In PWMC
		PF6000_FW6_FaultCodeList[70]	71	600	Transformer Cabinet Fan Config Error
		PF6000_FW6_FaultCodeList[71]	72	609	Line Over Voltage
		PF6000_FW6_FaultCodeList[72]	73	610	Line Neutral Over Voltage
		PF6000_FW6_FaultCodeList[73]	74	611	Line Short Circuit
		PF6000_FW6_FaultCodeList[74]	75	612	Line Voltage Unbalance
		PF6000_FW6_FaultCodeList[75]	76	613	Line Current Unbalance
		PF6000_FW6_FaultCodeList[76]	77	614	Line Side VSB Feedback Loss
		PF6000_FW6_FaultCodeList[77]	78	615	Fan Failure In Fan Group #4
		PF6000_FW6_FaultCodeList[78]	79	616	Pre-Charge Resistor Short Circuit
		PF6000_FW6_FaultCodeList[79]	80	617	VFD Over Current 2
		PF6000_FW6_FaultCodeList[80]	81	618	DC Bus Under Voltage Fault
		PF6000_FW6_FaultCodeList[81]	82	641	Input Circuit Breaker Tripped
		PF6000_FW6_FaultCodeList[82]	83	642	Transformer Over Temperature Trip
		PF6000_FW6_FaultCodeList[83]	84	643	Transformer Over Temperature Warning
		PF6000_FW6_FaultCodeList[84]	85	644	Power Cell Cabinet Fan Fault
		PF6000_FW6_FaultCodeList[85]	86	645	Power Cell Cabinet Fan CB Open
		PF6000_FW6_FaultCodeList[86]	87	646	Transformer Cabinet Fan Fault
		PF6000_FW6_FaultCodeList[87]	88	647	Transformer Cabinet Fan CB Open
		PF6000_FW6_FaultCodeList[88]	89	648	Auxiliary Power Off
		PF6000_FW6_FaultCodeList[89]	90	649	Cabinet Door Open
		PF6000_FW6_FaultCodeList[90]	91	650	External Control Power Loss Warning
		PF6000_FW6_FaultCodeList[91]	92	651	Analog Channel #1 Loss Warning
		PF6000_FW6_FaultCodeList[92]	93	652	DSP Communication Error
		PF6000_FW6_FaultCodeList[93]	94	653	Cooling Fan Contactor Open
		PF6000_FW6_FaultCodeList[94]	95	559	Versions Of System Not Compatible
		PF6000_FW6_FaultCodeList[95]	96	561	Overtemp Time Out In Power Cell #1
		PF6000_FW6_FaultCodeList[96]	97	562	Overtemp Time Out In Power Cell #2
		PF6000_FW6_FaultCodeList[97]	98	563	Overtemp Time Out In Power Cell #3
		PF6000_FW6_FaultCodeList[98]	99	564	Overtemp Time Out In Power Cell #4
		PF6000_FW6_FaultCodeList[99]	100	565	Overtemp Time Out In Power Cell #5
		PF6000_FW6_FaultCodeList[100]	101	566	Overtemp Time Out In Power Cell #6
		PF6000_FW6_FaultCodeList[101]	102	567	Overtemp Time Out In Power Cell #7
		PF6000_FW6_FaultCodeList[102]	103	568	Overtemp Time Out In Power Cell #8
		PF6000_FW6_FaultCodeList[103]	104	569	Overtemp Time Out In Power Cell #9
		PF6000_FW6_FaultCodeList[104]	105	570	Overtemp Time Out In Power Cell #10
		PF6000_FW6_FaultCodeList[105]	106	571	Overtemp Time Out In Power Cell #11
		PF6000_FW6_FaultCodeList[106]	107	572	Overtemp Time Out In Power Cell #12
		PF6000_FW6_FaultCodeList[107]	108	573	Overtemp Time Out In Power Cell #13
		PF6000_FW6_FaultCodeList[108]	109	574	Overtemp Time Out In Power Cell #14
		PF6000_FW6_FaultCodeList[109]	110	575	Overtemp Time Out In Power Cell #15
		PF6000_FW6_FaultCodeList[110]	111	576	Overtemp Time Out In Power Cell #16
		PF6000_FW6_FaultCodeList[111]	112	577	Overtemp Time Out In Power Cell #17
		PF6000_FW6_FaultCodeList[112]	113	578	Overtemp Time Out In Power Cell #18
		PF6000_FW6_FaultCodeList[113]	114	579	Overtemp Time Out In Power Cell #19
		PF6000_FW6_FaultCodeList[114]	115	580	Overtemp Time Out In Power Cell #20
		PF6000_FW6_FaultCodeList[115]	116	581	Overtemp Time Out In Power Cell #21
		PF6000_FW6_FaultCodeList[116]	117	582	Overtemp Time Out In Power Cell #22
		PF6000_FW6_FaultCodeList[117]	118	583	Overtemp Time Out In Power Cell #23
		PF6000_FW6_FaultCodeList[118]	119	584	Overtemp Time Out In Power Cell #24
		PF6000_FW6_FaultCodeList[119]	120	585	Overtemp Time Out In Power Cell #25
		PF6000_FW6_FaultCodeList[120]	121	586	Overtemp Time Out In Power Cell #26
		PF6000_FW6_FaultCodeList[121]	122	587	Overtemp Time Out In Power Cell #27
		PF6000_FW6_FaultCodeList[122]	123	1	IGBT Over Current In Power Cell #1
		PF6000_FW6_FaultCodeList[123]	124	2	Capacitor Abnormal In Power Cell #1
		PF6000_FW6_FaultCodeList[124]	125	3	Input Over Voltage In Power Cell #1
		PF6000_FW6_FaultCodeList[125]	126	4	DC Bus Undervoltage In Power Cell #1
		PF6000_FW6_FaultCodeList[126]	127	5	Communication Error In Power Cell #1
		PF6000_FW6_FaultCodeList[127]	128	6	No PWM Pulse For IGBT In Power Cell #1
		PF6000_FW6_FaultCodeList[128]	129	7	Bypass Hardware Fault In Power Cell #1
		PF6000_FW6_FaultCodeList[129]	130	8	Comm Link Fault In Power Cell #1
		PF6000_FW6_FaultCodeList[130]	131	9	PCCB Ver. Inompatible In Power Cell #1
		PF6000_FW6_FaultCodeList[131]	132	10	Power Cell #1 Bypassed
		PF6000_FW6_FaultCodeList[132]	133	11	Over Temperature In Power Cell #1
		PF6000_FW6_FaultCodeList[133]	134	12	Power Cell #1 Failed To Bypass
		PF6000_FW6_FaultCodeList[134]	135	13	One Phase Lost In Power Cell #1
		PF6000_FW6_FaultCodeList[135]	136	14	Two Phases Lost In Power Cell #1
		PF6000_FW6_FaultCodeList[136]	137	15	Bypass Failure (OV) In Power Cell #1
		PF6000_FW6_FaultCodeList[137]	138	17	IGBT Over Current In Power Cell #2
		PF6000_FW6_FaultCodeList[138]	139	18	Capacitor Abnormal In Power Cell #2
		PF6000_FW6_FaultCodeList[139]	140	19	Input Over Voltage In Power Cell #2
		PF6000_FW6_FaultCodeList[140]	141	20	DC Bus Undervoltage In Power Cell #2
		PF6000_FW6_FaultCodeList[141]	142	21	Communication Error In Power Cell #2
		PF6000_FW6_FaultCodeList[142]	143	22	No PWM Pulse For IGBT In Power Cell #2
		PF6000_FW6_FaultCodeList[143]	144	23	Bypass Hardware Fault In Power Cell #2
		PF6000_FW6_FaultCodeList[144]	145	24	Comm Link Fault in Power Cell #2
		PF6000_FW6_FaultCodeList[145]	146	25	PCCB Ver. Incompatible In Power Cell #2
		PF6000_FW6_FaultCodeList[146]	147	26	Power Cell #2 Bypassed
		PF6000_FW6_FaultCodeList[147]	148	27	Over Temperature In Power Cell #2
		PF6000_FW6_FaultCodeList[148]	149	28	Power Cell #2 Failed To Bypass
		PF6000_FW6_FaultCodeList[149]	150	29	One Phase Lost In Power Cell #2
		PF6000_FW6_FaultCodeList[150]	151	30	Two Phases Lost In Power Cell #2
		PF6000_FW6_FaultCodeList[151]	152	31	Bypass Failure (OV) In Power Cell #2
		PF6000_FW6_FaultCodeList[152]	153	33	IGBT Over Current In Power Cell #3
		PF6000_FW6_FaultCodeList[153]	154	34	Capacitor Abnormal In Power Cell #3
		PF6000_FW6_FaultCodeList[154]	155	35	Input Over Voltage In Power Cell #3
		PF6000_FW6_FaultCodeList[155]	156	36	DC Bus Undervoltage In Power Cell #3
		PF6000_FW6_FaultCodeList[156]	157	37	Communication Error In Power Cell #3
		PF6000_FW6_FaultCodeList[157]	158	38	No PWM Pulse For IGBT In Power Cell #3
		PF6000_FW6_FaultCodeList[158]	159	39	Bypass Hardware Fault In Power Cell #3
		PF6000_FW6_FaultCodeList[159]	160	40	Comm Link Fault in Power Cell #3
		PF6000_FW6_FaultCodeList[160]	161	41	PCCB Ver. Incompatible In Power Cell #3
		PF6000_FW6_FaultCodeList[161]	162	42	Power Cell #3 Bypassed
		PF6000_FW6_FaultCodeList[162]	163	43	Over Temperature In Power Cell #3
		PF6000_FW6_FaultCodeList[163]	164	44	Power Cell #3 Failed To Bypass
		PF6000_FW6_FaultCodeList[164]	165	45	One Phase Lost In Power Cell #3
		PF6000_FW6_FaultCodeList[165]	166	46	Two Phases Lost In Power Cell #3
		PF6000_FW6_FaultCodeList[166]	167	47	Bypass Failure (OV) In Power Cell #3
		PF6000_FW6_FaultCodeList[167]	168	49	IGBT Over Current In Power Cell #4
		PF6000_FW6_FaultCodeList[168]	169	50	Capacitor Abnormal In Power Cell #4
		PF6000_FW6_FaultCodeList[169]	170	51	Input Over Voltage In Power Cell #4
		PF6000_FW6_FaultCodeList[170]	171	52	DC Bus Undervoltage In Power Cell #4
		PF6000_FW6_FaultCodeList[171]	172	53	Communication Error In Power Cell #4
		PF6000_FW6_FaultCodeList[172]	173	54	No PWM Pulse For IGBT In Power Cell #4
		PF6000_FW6_FaultCodeList[173]	174	55	Bypass Hardware Fault In Power Cell #4
		PF6000_FW6_FaultCodeList[174]	175	56	Comm Link Fault in Power Cell #4
		PF6000_FW6_FaultCodeList[175]	176	57	PCCB Ver. Incompatible In Power Cell #4
		PF6000_FW6_FaultCodeList[176]	177	58	Power Cell #4 Bypassed
		PF6000_FW6_FaultCodeList[177]	178	59	Over Temperature In Power Cell #4
		PF6000_FW6_FaultCodeList[178]	179	60	Power Cell #4 Failed To Bypass
		PF6000_FW6_FaultCodeList[179]	180	61	One Phase Lost In Power Cell #4
		PF6000_FW6_FaultCodeList[180]	181	62	Two Phases Lost In Power Cell #4
		PF6000_FW6_FaultCodeList[181]	182	63	Bypass Failure (OV) In Power Cell #4
		PF6000_FW6_FaultCodeList[182]	183	65	IGBT Over Current In Power Cell #5
		PF6000_FW6_FaultCodeList[183]	184	66	Capacitor Abnormal In Power Cell #5
		PF6000_FW6_FaultCodeList[184]	185	67	Input Over Voltage In Power Cell #5
		PF6000_FW6_FaultCodeList[185]	186	68	DC Bus Undervoltage In Power Cell #5
		PF6000_FW6_FaultCodeList[186]	187	69	Communication Error In Power Cell #5
		PF6000_FW6_FaultCodeList[187]	188	70	No PWM Pulse For IGBT In Power Cell #5
		PF6000_FW6_FaultCodeList[188]	189	71	Bypass Hardware Fault In Power Cell #5
		PF6000_FW6_FaultCodeList[189]	190	72	Comm Link Fault in Power Cell #5
		PF6000_FW6_FaultCodeList[190]	191	73	PCCB Ver. Incompatible In Power Cell #5
		PF6000_FW6_FaultCodeList[191]	192	74	Power Cell #5 Bypassed
		PF6000_FW6_FaultCodeList[192]	193	75	Over Temperature In Power Cell #5
		PF6000_FW6_FaultCodeList[193]	194	76	Power Cell #5 Failed To Bypass
		PF6000_FW6_FaultCodeList[194]	195	77	One Phase Lost In Power Cell #5
		PF6000_FW6_FaultCodeList[195]	196	78	Two Phases Lost In Power Cell #5
		PF6000_FW6_FaultCodeList[196]	197	79	Bypass Failure (OV) In Power Cell #5
		PF6000_FW6_FaultCodeList[197]	198	81	IGBT Over Current In Power Cell #6
		PF6000_FW6_FaultCodeList[198]	199	82	Capacitor Abnormal In Power Cell #6
		PF6000_FW6_FaultCodeList[199]	200	83	Input Over Voltage In Power Cell #6
		PF6000_FW6_FaultCodeList[200]	201	84	DC Bus Undervoltage In Power Cell #6
		PF6000_FW6_FaultCodeList[201]	202	85	Communication Error In Power Cell #6
		PF6000_FW6_FaultCodeList[202]	203	86	No PWM Pulse For IGBT In Power Cell #6
		PF6000_FW6_FaultCodeList[203]	204	87	Bypass Hardware Fault In Power Cell #6
		PF6000_FW6_FaultCodeList[204]	205	88	Comm Link Fault in Power Cell #6
		PF6000_FW6_FaultCodeList[205]	206	89	PCCB Ver. Incompatible In Power Cell #6
		PF6000_FW6_FaultCodeList[206]	207	90	Power Cell #6 Bypassed
		PF6000_FW6_FaultCodeList[207]	208	91	Over Temperature In Power Cell #6
		PF6000_FW6_FaultCodeList[208]	209	92	Power Cell #6 Failed To Bypass
		PF6000_FW6_FaultCodeList[209]	210	93	One Phase Lost In Power Cell #6
		PF6000_FW6_FaultCodeList[210]	211	94	Two Phases Lost In Power Cell #6
		PF6000_FW6_FaultCodeList[211]	212	95	Bypass Failure (OV) In Power Cell #6
		PF6000_FW6_FaultCodeList[212]	213	97	IGBT Over Current In Power Cell #7
		PF6000_FW6_FaultCodeList[213]	214	98	Capacitor Abnormal In Power Cell #7
		PF6000_FW6_FaultCodeList[214]	215	99	Input Over Voltage In Power Cell #7
		PF6000_FW6_FaultCodeList[215]	216	100	DC Bus Undervoltage In Power Cell #7
		PF6000_FW6_FaultCodeList[216]	217	101	Communication Error In Power Cell #7
		PF6000_FW6_FaultCodeList[217]	218	102	No PWM Pulse For IGBT In Power Cell #7
		PF6000_FW6_FaultCodeList[218]	219	103	Bypass Hardware Fault In Power Cell #7
		PF6000_FW6_FaultCodeList[219]	220	104	Comm Link Fault in Power Cell #7
		PF6000_FW6_FaultCodeList[220]	221	105	PCCB Ver. Incompatible In Power Cell #7
		PF6000_FW6_FaultCodeList[221]	222	106	Power Cell #7 Bypassed
		PF6000_FW6_FaultCodeList[222]	223	107	Over Temperature In Power Cell #7
		PF6000_FW6_FaultCodeList[223]	224	108	Power Cell #7 Failed To Bypass
		PF6000_FW6_FaultCodeList[224]	225	109	One Phase Lost In Power Cell #7
		PF6000_FW6_FaultCodeList[225]	226	110	Two Phases Lost In Power Cell #7
		PF6000_FW6_FaultCodeList[226]	227	111	Bypass Failure (OV) In Power Cell #7
		PF6000_FW6_FaultCodeList[227]	228	113	IGBT Over Current In Power Cell #8
		PF6000_FW6_FaultCodeList[228]	229	114	Capacitor Abnormal In Power Cell #8
		PF6000_FW6_FaultCodeList[229]	230	115	Input Over Voltage In Power Cell #8
		PF6000_FW6_FaultCodeList[230]	231	116	DC Bus Undervoltage In Power Cell #8
		PF6000_FW6_FaultCodeList[231]	232	117	Communication Error In Power Cell #8
		PF6000_FW6_FaultCodeList[232]	233	118	No PWM Pulse For IGBT In Power Cell #8
		PF6000_FW6_FaultCodeList[233]	234	119	Bypass Hardware Fault In Power Cell #8
		PF6000_FW6_FaultCodeList[234]	235	120	Comm Link Fault in Power Cell #8
		PF6000_FW6_FaultCodeList[235]	236	121	PCCB Ver. Incompatible In Power Cell #8
		PF6000_FW6_FaultCodeList[236]	237	122	Power Cell #8 Bypassed
		PF6000_FW6_FaultCodeList[237]	238	123	Over Temperature In Power Cell #8
		PF6000_FW6_FaultCodeList[238]	239	124	Power Cell #8 Failed To Bypass
		PF6000_FW6_FaultCodeList[239]	240	125	One Phase Lost In Power Cell #8
		PF6000_FW6_FaultCodeList[240]	241	126	Two Phases Lost In Power Cell #8
		PF6000_FW6_FaultCodeList[241]	242	127	Bypass Failure (OV) In Power Cell #8
		PF6000_FW6_FaultCodeList[242]	243	129	IGBT Over Current In Power Cell #9
		PF6000_FW6_FaultCodeList[243]	244	130	Capacitor Abnormal In Power Cell #9
		PF6000_FW6_FaultCodeList[244]	245	131	Input Over Voltage In Power Cell #9
		PF6000_FW6_FaultCodeList[245]	246	132	DC Bus Undervoltage In Power Cell #9
		PF6000_FW6_FaultCodeList[246]	247	133	Communication Error In Power Cell #9
		PF6000_FW6_FaultCodeList[247]	248	134	No PWM Pulse For IGBT In Power Cell #9
		PF6000_FW6_FaultCodeList[248]	249	135	Bypass Hardware Fault In Power Cell #9
		PF6000_FW6_FaultCodeList[249]	250	136	Comm Link Fault in Power Cell #9
		PF6000_FW6_FaultCodeList[250]	251	137	PCCB Ver. Incompatible In Power Cell #9
		PF6000_FW6_FaultCodeList[251]	252	138	Power Cell #9 Bypassed
		PF6000_FW6_FaultCodeList[252]	253	139	Over Temperature In Power Cell #9
		PF6000_FW6_FaultCodeList[253]	254	140	Power Cell #9 Failed To Bypass
		PF6000_FW6_FaultCodeList[254]	255	141	One Phase Lost In Power Cell #9
		PF6000_FW6_FaultCodeList[255]	256	142	Two Phases Lost In Power Cell #9
		PF6000_FW6_FaultCodeList[256]	257	143	Bypass Failure (OV) In Power Cell #9
		PF6000_FW6_FaultCodeList[257]	258	145	IGBT Over Current In Power Cell #10
		PF6000_FW6_FaultCodeList[258]	259	146	Capacitor Abnormal In Power Cell #10
		PF6000_FW6_FaultCodeList[259]	260	147	Input Over Voltage In Power Cell #10
		PF6000_FW6_FaultCodeList[260]	261	148	DC Bus Undervoltage In Power Cell #10
		PF6000_FW6_FaultCodeList[261]	262	149	Communication Error In Power Cell #10
		PF6000_FW6_FaultCodeList[262]	263	150	No PWM Pulse For IGBT In Power Cell #10
		PF6000_FW6_FaultCodeList[263]	264	151	Bypass Hardware Fault In Power Cell #10
		PF6000_FW6_FaultCodeList[264]	265	152	Comm Link Fault in Power Cell #10
		PF6000_FW6_FaultCodeList[265]	266	153	PCCB Ver. Incompatible In Power Cell #10
		PF6000_FW6_FaultCodeList[266]	267	154	Power Cell #10 Bypassed
		PF6000_FW6_FaultCodeList[267]	268	155	Over Temperature In Power Cell #10
		PF6000_FW6_FaultCodeList[268]	269	156	Power Cell #10 Failed To Bypass
		PF6000_FW6_FaultCodeList[269]	270	157	One Phase Lost In Power Cell #10
		PF6000_FW6_FaultCodeList[270]	271	158	Two Phases Lost In Power Cell #10
		PF6000_FW6_FaultCodeList[271]	272	159	Bypass Failure (OV) In Power Cell #10
		PF6000_FW6_FaultCodeList[272]	273	161	IGBT Over Current In Power Cell #11
		PF6000_FW6_FaultCodeList[273]	274	162	Capacitor Abnormal In Power Cell #11
		PF6000_FW6_FaultCodeList[274]	275	163	Input Over Voltage In Power Cell #11
		PF6000_FW6_FaultCodeList[275]	276	164	DC Bus Undervoltage In Power Cell #11
		PF6000_FW6_FaultCodeList[276]	277	165	Communication Error In Power Cell #11
		PF6000_FW6_FaultCodeList[277]	278	166	No PWM Pulse For IGBT In Power Cell #11
		PF6000_FW6_FaultCodeList[278]	279	167	Bypass Hardware Fault In Power Cell #11
		PF6000_FW6_FaultCodeList[279]	280	168	Comm Link Fault in Power Cell #11
		PF6000_FW6_FaultCodeList[280]	281	169	PCCB Ver. Incompatible In Power Cell #11
		PF6000_FW6_FaultCodeList[281]	282	170	Power Cell #11 Bypassed
		PF6000_FW6_FaultCodeList[282]	283	171	Over Temperature In Power Cell #11
		PF6000_FW6_FaultCodeList[283]	284	172	Power Cell #11 Failed To Bypass
		PF6000_FW6_FaultCodeList[284]	285	173	One Phase Lost In Power Cell #11
		PF6000_FW6_FaultCodeList[285]	286	174	Two Phases Lost In Power Cell #11
		PF6000_FW6_FaultCodeList[286]	287	175	Bypass Failure (OV) In Power Cell #11
		PF6000_FW6_FaultCodeList[287]	288	177	IGBT Over Current In Power Cell #12
		PF6000_FW6_FaultCodeList[288]	289	178	Capacitor Abnormal In Power Cell #12
		PF6000_FW6_FaultCodeList[289]	290	179	Input Over Voltage In Power Cell #12
		PF6000_FW6_FaultCodeList[290]	291	180	DC Bus Undervoltage In Power Cell #12
		PF6000_FW6_FaultCodeList[291]	292	181	Communication Error In Power Cell #12
		PF6000_FW6_FaultCodeList[292]	293	182	No PWM Pulse For IGBT In Power Cell #12
		PF6000_FW6_FaultCodeList[293]	294	183	Bypass Hardware Fault In Power Cell #12
		PF6000_FW6_FaultCodeList[294]	295	184	Comm Link Fault in Power Cell #12
		PF6000_FW6_FaultCodeList[295]	296	185	PCCB Ver. Incompatible In Power Cell #12
		PF6000_FW6_FaultCodeList[296]	297	186	Power Cell #12 Bypassed
		PF6000_FW6_FaultCodeList[297]	298	187	Over Temperature In Power Cell #12
		PF6000_FW6_FaultCodeList[298]	299	188	Power Cell #12 Failed To Bypass
		PF6000_FW6_FaultCodeList[299]	300	189	One Phase Lost In Power Cell #12
		PF6000_FW6_FaultCodeList[300]	301	190	Two Phases Lost In Power Cell #12
		PF6000_FW6_FaultCodeList[301]	302	191	Bypass Failure (OV) In Power Cell #12
		PF6000_FW6_FaultCodeList[302]	303	193	IGBT Over Current In Power Cell #13
		PF6000_FW6_FaultCodeList[303]	304	194	Capacitor Abnormal In Power Cell #13
		PF6000_FW6_FaultCodeList[304]	305	195	Input Over Voltage In Power Cell #13
		PF6000_FW6_FaultCodeList[305]	306	196	DC Bus Undervoltage In Power Cell #13
		PF6000_FW6_FaultCodeList[306]	307	197	Communication Error In Power Cell #13
		PF6000_FW6_FaultCodeList[307]	308	198	No PWM Pulse For IGBT In Power Cell #13
		PF6000_FW6_FaultCodeList[308]	309	199	Bypass Hardware Fault In Power Cell #13
		PF6000_FW6_FaultCodeList[309]	310	200	Comm Link Fault in Power Cell #13
		PF6000_FW6_FaultCodeList[310]	311	201	PCCB Ver. Incompatible In Power Cell #13
		PF6000_FW6_FaultCodeList[311]	312	202	Power Cell #13 Bypassed
		PF6000_FW6_FaultCodeList[312]	313	203	Over Temperature In Power Cell #13
		PF6000_FW6_FaultCodeList[313]	314	204	Power Cell #13 Failed To Bypass
		PF6000_FW6_FaultCodeList[314]	315	205	One Phase Lost In Power Cell #13
		PF6000_FW6_FaultCodeList[315]	316	206	Two Phases Lost In Power Cell #13
		PF6000_FW6_FaultCodeList[316]	317	207	Bypass Failure (OV) In Power Cell #13
		PF6000_FW6_FaultCodeList[317]	318	209	IGBT Over Current In Power Cell #14
		PF6000_FW6_FaultCodeList[318]	319	210	Capacitor Abnormal In Power Cell #14
		PF6000_FW6_FaultCodeList[319]	320	211	Input Over Voltage In Power Cell #14
		PF6000_FW6_FaultCodeList[320]	321	212	DC Bus Undervoltage In Power Cell #14
		PF6000_FW6_FaultCodeList[321]	322	213	Communication Error In Power Cell #14
		PF6000_FW6_FaultCodeList[322]	323	214	No PWM Pulse For IGBT In Power Cell #14
		PF6000_FW6_FaultCodeList[323]	324	215	Bypass Hardware Fault In Power Cell #14
		PF6000_FW6_FaultCodeList[324]	325	216	Comm Link Fault in Power Cell #14
		PF6000_FW6_FaultCodeList[325]	326	217	PCCB Ver. Incompatible In Power Cell #14
		PF6000_FW6_FaultCodeList[326]	327	218	Power Cell #14 Bypassed
		PF6000_FW6_FaultCodeList[327]	328	219	Over Temperature In Power Cell #14
		PF6000_FW6_FaultCodeList[328]	329	220	Power Cell #14 Failed To Bypass
		PF6000_FW6_FaultCodeList[329]	330	221	One Phase Lost In Power Cell #14
		PF6000_FW6_FaultCodeList[330]	331	222	Two Phases Lost In Power Cell #14
		PF6000_FW6_FaultCodeList[331]	332	223	Bypass Failure (OV) In Power Cell #14
		PF6000_FW6_FaultCodeList[332]	333	225	IGBT Over Current In Power Cell #15
		PF6000_FW6_FaultCodeList[333]	334	226	Capacitor Abnormal In Power Cell #15
		PF6000_FW6_FaultCodeList[334]	335	227	Input Over Voltage In Power Cell #15
		PF6000_FW6_FaultCodeList[335]	336	228	DC Bus Undervoltage In Power Cell #15
		PF6000_FW6_FaultCodeList[336]	337	229	Communication Error In Power Cell #15
		PF6000_FW6_FaultCodeList[337]	338	230	No PWM Pulse For IGBT In Power Cell #15
		PF6000_FW6_FaultCodeList[338]	339	231	Bypass Hardware Fault In Power Cell #15
		PF6000_FW6_FaultCodeList[339]	340	232	Comm Link Fault in Power Cell #15
		PF6000_FW6_FaultCodeList[340]	341	233	PCCB Ver. Incompatible In Power Cell #15
		PF6000_FW6_FaultCodeList[341]	342	234	Power Cell #15 Bypassed
		PF6000_FW6_FaultCodeList[342]	343	235	Over Temperature In Power Cell #15
		PF6000_FW6_FaultCodeList[343]	344	236	Power Cell #15 Failed To Bypass
		PF6000_FW6_FaultCodeList[344]	345	237	One Phase Lost In Power Cell #15
		PF6000_FW6_FaultCodeList[345]	346	238	Two Phases Lost In Power Cell #15
		PF6000_FW6_FaultCodeList[346]	347	239	Bypass Failure (OV) In Power Cell #15
		PF6000_FW6_FaultCodeList[347]	348	241	IGBT Over Current In Power Cell #16
		PF6000_FW6_FaultCodeList[348]	349	242	Capacitor Abnormal In Power Cell #16
		PF6000_FW6_FaultCodeList[349]	350	243	Input Over Voltage In Power Cell #16
		PF6000_FW6_FaultCodeList[350]	351	244	DC Bus Undervoltage In Power Cell #16
		PF6000_FW6_FaultCodeList[351]	352	245	Communication Error In Power Cell #16
		PF6000_FW6_FaultCodeList[352]	353	246	No PWM Pulse For IGBT In Power Cell #16
		PF6000_FW6_FaultCodeList[353]	354	247	Bypass Hardware Fault In Power Cell #16
		PF6000_FW6_FaultCodeList[354]	355	248	Comm Link Fault in Power Cell #16
		PF6000_FW6_FaultCodeList[355]	356	249	PCCB Ver. Incompatible In Power Cell #16
		PF6000_FW6_FaultCodeList[356]	357	250	Power Cell #16 Bypassed
		PF6000_FW6_FaultCodeList[357]	358	251	Over Temperature In Power Cell #16
		PF6000_FW6_FaultCodeList[358]	359	252	Power Cell #16 Failed To Bypass
		PF6000_FW6_FaultCodeList[359]	360	253	One Phase Lost In Power Cell #16
		PF6000_FW6_FaultCodeList[360]	361	254	Two Phases Lost In Power Cell #16
		PF6000_FW6_FaultCodeList[361]	362	255	Bypass Failure (OV) In Power Cell #16
		PF6000_FW6_FaultCodeList[362]	363	257	IGBT Over Current In Power Cell #17
		PF6000_FW6_FaultCodeList[363]	364	258	Capacitor Abnormal In Power Cell #17
		PF6000_FW6_FaultCodeList[364]	365	259	Input Over Voltage In Power Cell #17
		PF6000_FW6_FaultCodeList[365]	366	260	DC Bus Undervoltage In Power Cell #17
		PF6000_FW6_FaultCodeList[366]	367	261	Communication Error In Power Cell #17
		PF6000_FW6_FaultCodeList[367]	368	262	No PWM Pulse For IGBT In Power Cell #17
		PF6000_FW6_FaultCodeList[368]	369	263	Bypass Hardware Fault In Power Cell #17
		PF6000_FW6_FaultCodeList[369]	370	264	Comm Link Fault in Power Cell #17
		PF6000_FW6_FaultCodeList[370]	371	265	PCCB Ver. Incompatible In Power Cell #17
		PF6000_FW6_FaultCodeList[371]	372	266	Power Cell #17 Bypassed
		PF6000_FW6_FaultCodeList[372]	373	267	Over Temperature In Power Cell #17
		PF6000_FW6_FaultCodeList[373]	374	268	Power Cell #17 Failed To Bypass
		PF6000_FW6_FaultCodeList[374]	375	269	One Phase Lost In Power Cell #17
		PF6000_FW6_FaultCodeList[375]	376	270	Two Phases Lost In Power Cell #17
		PF6000_FW6_FaultCodeList[376]	377	271	Bypass Failure (OV) In Power Cell #17
		PF6000_FW6_FaultCodeList[377]	378	273	IGBT Over Current In Power Cell #18
		PF6000_FW6_FaultCodeList[378]	379	274	Capacitor Abnormal In Power Cell #18
		PF6000_FW6_FaultCodeList[379]	380	275	Input Over Voltage In Power Cell #18
		PF6000_FW6_FaultCodeList[380]	381	276	DC Bus Undervoltage In Power Cell #18
		PF6000_FW6_FaultCodeList[381]	382	277	Communication Error In Power Cell #18
		PF6000_FW6_FaultCodeList[382]	383	278	No PWM Pulse For IGBT In Power Cell #18
		PF6000_FW6_FaultCodeList[383]	384	279	Bypass Hardware Fault In Power Cell #18
		PF6000_FW6_FaultCodeList[384]	385	280	Comm Link Fault in Power Cell #18
		PF6000_FW6_FaultCodeList[385]	386	281	PCCB Ver. Incompatible In Power Cell #18
		PF6000_FW6_FaultCodeList[386]	387	282	Power Cell #18 Bypassed
		PF6000_FW6_FaultCodeList[387]	388	283	Over Temperature In Power Cell #18
		PF6000_FW6_FaultCodeList[388]	389	284	Power Cell #18 Failed To Bypass
		PF6000_FW6_FaultCodeList[389]	390	285	One Phase Lost In Power Cell #18
		PF6000_FW6_FaultCodeList[390]	391	286	Two Phases Lost In Power Cell #18
		PF6000_FW6_FaultCodeList[391]	392	287	Bypass Failure (OV) In Power Cell #18
		PF6000_FW6_FaultCodeList[392]	393	289	IGBT Over Current In Power Cell #19
		PF6000_FW6_FaultCodeList[393]	394	290	Capacitor Abnormal In Power Cell #19
		PF6000_FW6_FaultCodeList[394]	395	291	Input Over Voltage In Power Cell #19
		PF6000_FW6_FaultCodeList[395]	396	292	DC Bus Undervoltage In Power Cell #19
		PF6000_FW6_FaultCodeList[396]	397	293	Communication Error In Power Cell #19
		PF6000_FW6_FaultCodeList[397]	398	294	No PWM Pulse For IGBT In Power Cell #19
		PF6000_FW6_FaultCodeList[398]	399	295	Bypass Hardware Fault In Power Cell #19
		PF6000_FW6_FaultCodeList[399]	400	296	Comm Link Fault in Power Cell #19
		PF6000_FW6_FaultCodeList[400]	401	297	PCCB Ver. Incompatible In Power Cell #19
		PF6000_FW6_FaultCodeList[401]	402	298	Power Cell #19 Bypassed
		PF6000_FW6_FaultCodeList[402]	403	299	Over Temperature In Power Cell #19
		PF6000_FW6_FaultCodeList[403]	404	300	Power Cell #19 Failed To Bypass
		PF6000_FW6_FaultCodeList[404]	405	301	One Phase Lost In Power Cell #19
		PF6000_FW6_FaultCodeList[405]	406	302	Two Phases Lost In Power Cell #19
		PF6000_FW6_FaultCodeList[406]	407	303	Bypass Failure (OV) In Power Cell #19
		PF6000_FW6_FaultCodeList[407]	408	305	IGBT Over Current In Power Cell #20
		PF6000_FW6_FaultCodeList[408]	409	306	Capacitor Abnormal In Power Cell #20
		PF6000_FW6_FaultCodeList[409]	410	307	Input Over Voltage In Power Cell #20
		PF6000_FW6_FaultCodeList[410]	411	308	DC Bus Undervoltage In Power Cell #20
		PF6000_FW6_FaultCodeList[411]	412	309	Communication Error In Power Cell #20
		PF6000_FW6_FaultCodeList[412]	413	310	No PWM Pulse For IGBT In Power Cell #20
		PF6000_FW6_FaultCodeList[413]	414	311	Bypass Hardware Fault In Power Cell #20
		PF6000_FW6_FaultCodeList[414]	415	312	Comm Link Fault in Power Cell #20
		PF6000_FW6_FaultCodeList[415]	416	313	PCCB Ver. Incompatible In Power Cell #20
		PF6000_FW6_FaultCodeList[416]	417	314	Power Cell #20 Bypassed
		PF6000_FW6_FaultCodeList[417]	418	315	Over Temperature In Power Cell #20
		PF6000_FW6_FaultCodeList[418]	419	316	Power Cell #20 Failed To Bypass
		PF6000_FW6_FaultCodeList[419]	420	317	One Phase Lost In Power Cell #20
		PF6000_FW6_FaultCodeList[420]	421	318	Two Phases Lost In Power Cell #20
		PF6000_FW6_FaultCodeList[421]	422	319	Bypass Failure (OV) In Power Cell #20
		PF6000_FW6_FaultCodeList[422]	423	321	IGBT Over Current In Power Cell #21
		PF6000_FW6_FaultCodeList[423]	424	322	Capacitor Abnormal In Power Cell #21
		PF6000_FW6_FaultCodeList[424]	425	323	Input Over Voltage In Power Cell #21
		PF6000_FW6_FaultCodeList[425]	426	324	DC Bus Undervoltage In Power Cell #21
		PF6000_FW6_FaultCodeList[426]	427	325	Communication Error In Power Cell #21
		PF6000_FW6_FaultCodeList[427]	428	326	No PWM Pulse For IGBT In Power Cell #21
		PF6000_FW6_FaultCodeList[428]	429	327	Bypass Hardware Fault In Power Cell #21
		PF6000_FW6_FaultCodeList[429]	430	328	Comm Link Fault in Power Cell #21
		PF6000_FW6_FaultCodeList[430]	431	329	PCCB Ver. Incompatible In Power Cell #21
		PF6000_FW6_FaultCodeList[431]	432	330	Power Cell #21 Bypassed
		PF6000_FW6_FaultCodeList[432]	433	331	Over Temperature In Power Cell #21
		PF6000_FW6_FaultCodeList[433]	434	332	Power Cell #21 Failed To Bypass
		PF6000_FW6_FaultCodeList[434]	435	333	One Phase Lost In Power Cell #21
		PF6000_FW6_FaultCodeList[435]	436	334	Two Phases Lost In Power Cell #21
		PF6000_FW6_FaultCodeList[436]	437	335	Bypass Failure (OV) In Power Cell #21
		PF6000_FW6_FaultCodeList[437]	438	337	IGBT Over Current In Power Cell #22
		PF6000_FW6_FaultCodeList[438]	439	338	Capacitor Abnormal In Power Cell #22
		PF6000_FW6_FaultCodeList[439]	440	339	Input Over Voltage In Power Cell #22
		PF6000_FW6_FaultCodeList[440]	441	340	DC Bus Undervoltage In Power Cell #22
		PF6000_FW6_FaultCodeList[441]	442	341	Communication Error In Power Cell #22
		PF6000_FW6_FaultCodeList[442]	443	342	No PWM Pulse For IGBT In Power Cell #22
		PF6000_FW6_FaultCodeList[443]	444	343	Bypass Hardware Fault In Power Cell #22
		PF6000_FW6_FaultCodeList[444]	445	344	Comm Link Fault in Power Cell #22
		PF6000_FW6_FaultCodeList[445]	446	345	PCCB Ver. Incompatible In Power Cell #22
		PF6000_FW6_FaultCodeList[446]	447	346	Power Cell #22 Bypassed
		PF6000_FW6_FaultCodeList[447]	448	347	Over Temperature In Power Cell #22
		PF6000_FW6_FaultCodeList[448]	449	348	Power Cell #22 Failed To Bypass
		PF6000_FW6_FaultCodeList[449]	450	349	One Phase Lost In Power Cell #22
		PF6000_FW6_FaultCodeList[450]	451	350	Two Phases Lost In Power Cell #22
		PF6000_FW6_FaultCodeList[451]	452	351	Bypass Failure (OV) In Power Cell #22
		PF6000_FW6_FaultCodeList[452]	453	353	IGBT Over Current In Power Cell #23
		PF6000_FW6_FaultCodeList[453]	454	354	Capacitor Abnormal In Power Cell #23
		PF6000_FW6_FaultCodeList[454]	455	355	Input Over Voltage In Power Cell #23
		PF6000_FW6_FaultCodeList[455]	456	356	DC Bus Undervoltage In Power Cell #23
		PF6000_FW6_FaultCodeList[456]	457	357	Communication Error In Power Cell #23
		PF6000_FW6_FaultCodeList[457]	458	358	No PWM Pulse For IGBT In Power Cell #23
		PF6000_FW6_FaultCodeList[458]	459	359	Bypass Hardware Fault In Power Cell #23
		PF6000_FW6_FaultCodeList[459]	460	360	Comm Link Fault in Power Cell #23
		PF6000_FW6_FaultCodeList[460]	461	361	PCCB Ver. Incompatible In Power Cell #23
		PF6000_FW6_FaultCodeList[461]	462	362	Power Cell #23 Bypassed
		PF6000_FW6_FaultCodeList[462]	463	363	Over Temperature In Power Cell #23
		PF6000_FW6_FaultCodeList[463]	464	364	Power Cell #23 Failed To Bypass
		PF6000_FW6_FaultCodeList[464]	465	365	One Phase Lost In Power Cell #23
		PF6000_FW6_FaultCodeList[465]	466	366	Two Phases Lost In Power Cell #23
		PF6000_FW6_FaultCodeList[466]	467	367	Bypass Failure (OV) In Power Cell #23
		PF6000_FW6_FaultCodeList[467]	468	369	IGBT Over Current In Power Cell #24
		PF6000_FW6_FaultCodeList[468]	469	370	Capacitor Abnormal In Power Cell #24
		PF6000_FW6_FaultCodeList[469]	470	371	Input Over Voltage In Power Cell #24
		PF6000_FW6_FaultCodeList[470]	471	372	DC Bus Undervoltage In Power Cell #24
		PF6000_FW6_FaultCodeList[471]	472	373	Communication Error In Power Cell #24
		PF6000_FW6_FaultCodeList[472]	473	374	No PWM Pulse For IGBT In Power Cell #24
		PF6000_FW6_FaultCodeList[473]	474	375	Bypass Hardware Fault In Power Cell #24
		PF6000_FW6_FaultCodeList[474]	475	376	Comm Link Fault in Power Cell #24
		PF6000_FW6_FaultCodeList[475]	476	377	PCCB Ver. Incompatible In Power Cell #24
		PF6000_FW6_FaultCodeList[476]	477	378	Power Cell #24 Bypassed
		PF6000_FW6_FaultCodeList[477]	478	379	Over Temperature In Power Cell #24
		PF6000_FW6_FaultCodeList[478]	479	380	Power Cell #24 Failed To Bypass
		PF6000_FW6_FaultCodeList[479]	480	381	One Phase Lost In Power Cell #24
		PF6000_FW6_FaultCodeList[480]	481	382	Two Phases Lost In Power Cell #24
		PF6000_FW6_FaultCodeList[481]	482	383	Bypass Failure (OV) In Power Cell #24
		PF6000_FW6_FaultCodeList[482]	483	385	IGBT Over Current In Power Cell #25
		PF6000_FW6_FaultCodeList[483]	484	386	Capacitor Abnormal In Power Cell #25
		PF6000_FW6_FaultCodeList[484]	485	387	Input Over Voltage In Power Cell #25
		PF6000_FW6_FaultCodeList[485]	486	388	DC Bus Undervoltage In Power Cell #25
		PF6000_FW6_FaultCodeList[486]	487	389	Communication Error In Power Cell #25
		PF6000_FW6_FaultCodeList[487]	488	390	No PWM Pulse For IGBT In Power Cell #25
		PF6000_FW6_FaultCodeList[488]	489	391	Bypass Hardware Fault In Power Cell #25
		PF6000_FW6_FaultCodeList[489]	490	392	Comm Link Fault in Power Cell #25
		PF6000_FW6_FaultCodeList[490]	491	393	PCCB Ver. Incompatible In Power Cell #25
		PF6000_FW6_FaultCodeList[491]	492	394	Power Cell #25 Bypassed
		PF6000_FW6_FaultCodeList[492]	493	395	Over Temperature In Power Cell #25
		PF6000_FW6_FaultCodeList[493]	494	396	Power Cell #25 Failed To Bypass
		PF6000_FW6_FaultCodeList[494]	495	397	One Phase Lost In Power Cell #25
		PF6000_FW6_FaultCodeList[495]	496	398	Two Phases Lost In Power Cell #25
		PF6000_FW6_FaultCodeList[496]	497	399	Bypass Failure (OV) In Power Cell #25
		PF6000_FW6_FaultCodeList[497]	498	401	IGBT Over Current In Power Cell #26
		PF6000_FW6_FaultCodeList[498]	499	402	Capacitor Abnormal In Power Cell #26
		PF6000_FW6_FaultCodeList[499]	500	403	Input Over Voltage In Power Cell #26
		PF6000_FW6_FaultCodeList[500]	501	404	DC Bus Undervoltage In Power Cell #26
		PF6000_FW6_FaultCodeList[501]	502	405	Communication Error In Power Cell #26
		PF6000_FW6_FaultCodeList[502]	503	406	No PWM Pulse For IGBT In Power Cell #26
		PF6000_FW6_FaultCodeList[503]	504	407	Bypass Hardware Fault In Power Cell #26
		PF6000_FW6_FaultCodeList[504]	505	408	Comm Link Fault in Power Cell #26
		PF6000_FW6_FaultCodeList[505]	506	409	PCCB Ver. Incompatible In Power Cell #26
		PF6000_FW6_FaultCodeList[506]	507	410	Power Cell #26 Bypassed
		PF6000_FW6_FaultCodeList[507]	508	411	Over Temperature In Power Cell #26
		PF6000_FW6_FaultCodeList[508]	509	412	Power Cell #26 Failed To Bypass
		PF6000_FW6_FaultCodeList[509]	510	413	One Phase Lost In Power Cell #26
		PF6000_FW6_FaultCodeList[510]	511	414	Two Phases Lost In Power Cell #26
		PF6000_FW6_FaultCodeList[511]	512	415	Bypass Failure (OV) In Power Cell #26
		PF6000_FW6_FaultCodeList[512]	513	417	IGBT Over Current In Power Cell #27
		PF6000_FW6_FaultCodeList[513]	514	418	Capacitor Abnormal In Power Cell #27
		PF6000_FW6_FaultCodeList[514]	515	419	Input Over Voltage In Power Cell #27
		PF6000_FW6_FaultCodeList[515]	516	420	DC Bus Undervoltage In Power Cell #27
		PF6000_FW6_FaultCodeList[516]	517	421	Communication Error In Power Cell #27
		PF6000_FW6_FaultCodeList[517]	518	422	No PWM Pulse For IGBT In Power Cell #27
		PF6000_FW6_FaultCodeList[518]	519	423	Bypass Hardware Fault In Power Cell #27
		PF6000_FW6_FaultCodeList[519]	520	424	Comm Link Fault in Power Cell #27
		PF6000_FW6_FaultCodeList[520]	521	425	PCCB Ver. Incompatible In Power Cell #27
		PF6000_FW6_FaultCodeList[521]	522	426	Power Cell #27 Bypassed
		PF6000_FW6_FaultCodeList[522]	523	427	Over Temperature In Power Cell #27
		PF6000_FW6_FaultCodeList[523]	524	428	Power Cell #27 Failed To Bypass
		PF6000_FW6_FaultCodeList[524]	525	429	One Phase Lost In Power Cell #27
		PF6000_FW6_FaultCodeList[525]	526	430	Two Phases Lost In Power Cell #27
		PF6000_FW6_FaultCodeList[526]	527	431	Bypass Failure (OV) In Power Cell #27
		PF6000_FW6_FaultCodeList[527]	528	497	PWMA Board Not Compatible With PCCBA1
		PF6000_FW6_FaultCodeList[528]	529	498	PWMA Board Not Compatible With PCCBA2
		PF6000_FW6_FaultCodeList[529]	530	499	PWMA Board Not Compatible With PCCBA3
		PF6000_FW6_FaultCodeList[530]	531	500	PWMA Board Not Compatible With PCCBA4
		PF6000_FW6_FaultCodeList[531]	532	501	PWMA Board Not Compatible With PCCBA5
		PF6000_FW6_FaultCodeList[532]	533	502	PWMA Board Not Compatible With PCCBA6
		PF6000_FW6_FaultCodeList[533]	534	503	PWMA Board Not Compatible With PCCBA7
		PF6000_FW6_FaultCodeList[534]	535	504	PWMA Board Not Compatible With PCCBA8
		PF6000_FW6_FaultCodeList[535]	536	505	PWMA Board Not Compatible With PCCBA9
		PF6000_FW6_FaultCodeList[536]	537	513	PWMB Board Not Compatible With PCCBB1
		PF6000_FW6_FaultCodeList[537]	538	514	PWMB Board Not Compatible With PCCBB2
		PF6000_FW6_FaultCodeList[538]	539	515	PWMB Board Not Compatible With PCCBB3
		PF6000_FW6_FaultCodeList[539]	540	516	PWMB Board Not Compatible With PCCBB4
		PF6000_FW6_FaultCodeList[540]	541	517	PWMB Board Not Compatible With PCCBB5
		PF6000_FW6_FaultCodeList[541]	542	518	PWMB Board Not Compatible With PCCBB6
		PF6000_FW6_FaultCodeList[542]	543	519	PWMB Board Not Compatible With PCCBB7
		PF6000_FW6_FaultCodeList[543]	544	520	PWMB Board Not Compatible With PCCBB8
		PF6000_FW6_FaultCodeList[544]	545	521	PWMB Board Not Compatible With PCCBB9
		PF6000_FW6_FaultCodeList[545]	546	529	PWMC Board Not Compatible With PCCBC1
		PF6000_FW6_FaultCodeList[546]	547	530	PWMC Board Not Compatible With PCCBC2
		PF6000_FW6_FaultCodeList[547]	548	531	PWMC Board Not Compatible With PCCBC3
		PF6000_FW6_FaultCodeList[548]	549	532	PWMC Board Not Compatible With PCCBC4
		PF6000_FW6_FaultCodeList[549]	550	533	PWMC Board Not Compatible With PCCBC5
		PF6000_FW6_FaultCodeList[550]	551	534	PWMC Board Not Compatible With PCCBC6
		PF6000_FW6_FaultCodeList[551]	552	535	PWMC Board Not Compatible With PCCBC7
		PF6000_FW6_FaultCodeList[552]	553	536	PWMC Board Not Compatible With PCCBC8
		PF6000_FW6_FaultCodeList[553]	554	537	PWMC Board Not Compatible With PCCBC9
		PF6000_FW6_FaultCodeList[554]	555	545	Primary FPGA Not Compatible With PWMA
		PF6000_FW6_FaultCodeList[555]	556	546	Primary FPGA Not Compatible With PWMB
		PF6000_FW6_FaultCodeList[556]	557	547	Primary FPGA Not Compatible With PWMC
		PF6000_FW6_FaultCodeList[557]	558	548	Primary FPGA Not Compatible With DT
		PF6000_FW6_FaultCodeList[558]	559	549	Pri. DSP Not Compatible With Pri. FPGA
		PF6000_FW6_FaultCodeList[559]	560	550	Pri. DSP Not Compatible With Sec. DSP
		PF6000_FW6_FaultCodeList[560]	561	553	Primary DSP Not Compatible With PLC
		PF6000_FW6_FaultCodeList[561]	562	673	User Defined Fault #1
		PF6000_FW6_FaultCodeList[562]	563	674	User Defined Fault #2
		PF6000_FW6_FaultCodeList[563]	564	675	User Defined Fault #3
		PF6000_FW6_FaultCodeList[564]	565	676	User Defined Fault #4
		PF6000_FW6_FaultCodeList[565]	566	677	User Defined Fault #5
		PF6000_FW6_FaultCodeList[566]	567	678	User Defined Fault #6
		PF6000_FW6_FaultCodeList[567]	568	679	User Defined Fault #7
		PF6000_FW6_FaultCodeList[568]	569	680	User Defined Fault #8
		PF6000_FW6_FaultCodeList[569]	570	681	User Defined Fault #9
		PF6000_FW6_FaultCodeList[570]	571	682	User Defined Fault #10
		PF6000_FW6_FaultCodeList[571]	572	683	User Defined Fault #11
		PF6000_FW6_FaultCodeList[572]	573	684	User Defined Fault #12
		PF6000_FW6_FaultCodeList[573]	574	685	User Defined Fault #13
		PF6000_FW6_FaultCodeList[574]	575	686	User Defined Fault #14
		PF6000_FW6_FaultCodeList[575]	576	687	User Defined Fault #15
		PF6000_FW6_FaultCodeList[576]	577	688	User Defined Fault #16
		PF6000_FW6_FaultCodeList[577]	578	689	User Defined Warning #1
		PF6000_FW6_FaultCodeList[578]	579	690	User Defined Warning #2
		PF6000_FW6_FaultCodeList[579]	580	691	User Defined Warning #3
		PF6000_FW6_FaultCodeList[580]	581	692	User Defined Warning #4
		PF6000_FW6_FaultCodeList[581]	582	693	User Defined Warning #5
		PF6000_FW6_FaultCodeList[582]	583	694	User Defined Warning #6
		PF6000_FW6_FaultCodeList[583]	584	695	User Defined Warning #7
		PF6000_FW6_FaultCodeList[584]	585	696	User Defined Warning #8
		PF6000_FW6_FaultCodeList[585]	586	697	User Defined Warning #9
		PF6000_FW6_FaultCodeList[586]	587	698	User Defined Warning #10
		PF6000_FW6_FaultCodeList[587]	588	699	User Defined Warning #11
		PF6000_FW6_FaultCodeList[588]	589	700	User Defined Warning #12
		PF6000_FW6_FaultCodeList[589]	590	701	User Defined Warning #13
		PF6000_FW6_FaultCodeList[590]	591	702	User Defined Warning #14
		PF6000_FW6_FaultCodeList[591]	592	703	User Defined Warning #15
		PF6000_FW6_FaultCodeList[592]	593	704	User Defined Warning #16

## PF7xx
	PF7xx_FaultCodeList	Read From CLX:
		Send To CLX:
	Fault codes and text for
	PowerFlex 70, 70EC, 700 series drives	Description:		Fault Code	Description for given Fault Code
	(except PF700S)	Usage:		UDT	UDT
		Data Type:		DINT	STRING_40
			(Origin)	.	.
Unit	Tag Description	TagName	Instance	Code	Desc
		Default Values:	0	0	Check drive manual for this fault code
		PF7xx_FaultCodeList[0]	1	0	Check drive manual for this fault code
		PF7xx_FaultCodeList[1]	2	121	I/O Communication Loss
		PF7xx_FaultCodeList[2]	3	122	I/O Failure
		PF7xx_FaultCodeList[3]	4	91	Encoder Loss
		PF7xx_FaultCodeList[4]	5		Pulse Input Loss
		PF7xx_FaultCodeList[5]	6	93	Hardware Fault
		PF7xx_FaultCodeList[6]	7	94	Hardware Enable Missing
		PF7xx_FaultCodeList[7]	8	1	Precharge Active
		PF7xx_FaultCodeList[8]	9	2	Auxiliary Input
		PF7xx_FaultCodeList[9]	10	3	Power Loss
		PF7xx_FaultCodeList[10]	11	4	Under Voltage
		PF7xx_FaultCodeList[11]	12	5	Over Voltage
		PF7xx_FaultCodeList[12]	13	6	Motor Stall
		PF7xx_FaultCodeList[13]	14	7	Motor Overload
		PF7xx_FaultCodeList[14]	15	8	Heatsink OverTemp
		PF7xx_FaultCodeList[15]	16	9	IGBT OverTemp
		PF7xx_FaultCodeList[16]	17	10	System Fault
		PF7xx_FaultCodeList[17]	18	12	Hardware Overcurrent
		PF7xx_FaultCodeList[18]	19	13	Ground Fault
		PF7xx_FaultCodeList[19]	20	14	Inverter Fault
		PF7xx_FaultCodeList[20]	21	15	Load Loss
		PF7xx_FaultCodeList[21]	22	16	Motor Thermistor
		PF7xx_FaultCodeList[22]	23	17	Input Phase Loss
		PF7xx_FaultCodeList[23]	24	19	Unbalanced Power
		PF7xx_FaultCodeList[24]	25	20	Torque Prover Speed Band
		PF7xx_FaultCodeList[25]	26	21	Output Phase Loss
		PF7xx_FaultCodeList[26]	27	22	Nameplate Hz Conflict
		PF7xx_FaultCodeList[27]	28	23	Max Frequency Conflict
		PF7xx_FaultCodeList[28]	29	24	Decel Inhibit
		PF7xx_FaultCodeList[29]	30	25	Over Speed Limit
		PF7xx_FaultCodeList[30]	31	26	VHz Negative Slope
		PF7xx_FaultCodeList[31]	32	27	Speed Reference Conflict
		PF7xx_FaultCodeList[32]	33	28	Braking Resistor Missing
		PF7xx_FaultCodeList[33]	34	29	Analog Input Loss
		PF7xx_FaultCodeList[34]	35	31	IGBT Temperature HW
		PF7xx_FaultCodeList[35]	36	32	Fan Cooling Fault
		PF7xx_FaultCodeList[36]	37	33	Auto Restart Tries
		PF7xx_FaultCodeList[37]	38	34	CAN Bus Fault
		PF7xx_FaultCodeList[38]	39	36	Software Overcurrent
		PF7xx_FaultCodeList[39]	40	37	Heatsink Under Temperature
		PF7xx_FaultCodeList[40]	41	38	Phase U to Ground
		PF7xx_FaultCodeList[41]	42	39	Phase V to Ground
		PF7xx_FaultCodeList[42]	43	40	Phase W to Ground
		PF7xx_FaultCodeList[43]	44	41	Phase U-V Short
		PF7xx_FaultCodeList[44]	45	42	Phase U-W Short
		PF7xx_FaultCodeList[45]	46	43	Phase V-W Short
		PF7xx_FaultCodeList[46]	47	44	Device Changed
		PF7xx_FaultCodeList[47]	48	45	Device Added
		PF7xx_FaultCodeList[48]	49	47	NVS Read Checksum
		PF7xx_FaultCodeList[49]	50	48	Params Defaulted
		PF7xx_FaultCodeList[50]	51	48	Params Defaulted
		PF7xx_FaultCodeList[51]	52	49	Drive Powerup
		PF7xx_FaultCodeList[52]	53	51	Fault Queue Cleared
		PF7xx_FaultCodeList[53]	54	52	Faults Cleared
		PF7xx_FaultCodeList[54]	55	55	Control Board Overtemp
		PF7xx_FaultCodeList[55]	56	59	Gate Disable
		PF7xx_FaultCodeList[56]	57	60	Hardware Thermistor
		PF7xx_FaultCodeList[57]	58	63	Shear Pin
		PF7xx_FaultCodeList[58]	59	64	Drive Overload
		PF7xx_FaultCodeList[59]	60	65	I/O Removed
		PF7xx_FaultCodeList[60]	61	69	D B Resistance
		PF7xx_FaultCodeList[61]	62	70	Power Unit Fault
		PF7xx_FaultCodeList[62]	63	71	Port 1 Adapter
		PF7xx_FaultCodeList[63]	64	72	Port 2 Adapter
		PF7xx_FaultCodeList[64]	65	73	Port 3 Adapter
		PF7xx_FaultCodeList[65]	66	74	Port 4 Adapter
		PF7xx_FaultCodeList[66]	67	75	Port 5 Adapter
		PF7xx_FaultCodeList[67]	68	76	Port 6 Adapter
		PF7xx_FaultCodeList[68]	69	77	IR Volts Range
		PF7xx_FaultCodeList[69]	70	78	Flux Amps Ref Range
		PF7xx_FaultCodeList[70]	71	79	Excessive Load
		PF7xx_FaultCodeList[71]	72	80	AutoTune Aborted
		PF7xx_FaultCodeList[72]	73	81	Port 1 DPI Loss
		PF7xx_FaultCodeList[73]	74	82	Port 2 DPI Loss
		PF7xx_FaultCodeList[74]	75	83	Port 3 DPI Loss
		PF7xx_FaultCodeList[75]	76	84	Port 4 DPI Loss
		PF7xx_FaultCodeList[76]	77	85	Port 5 DPI Loss
		PF7xx_FaultCodeList[77]	78	86	Port 6 DPI Loss
		PF7xx_FaultCodeList[78]	79	87	IXo Voltage Range
		PF7xx_FaultCodeList[79]	80	88	Software Fault
		PF7xx_FaultCodeList[80]	81	89	Software Fault
		PF7xx_FaultCodeList[81]	82	90	Encoder Quad Error
		PF7xx_FaultCodeList[82]	83	95	AutoTune Rs Static Test Fail
		PF7xx_FaultCodeList[83]	84	96	AutoTune Rm Rotate Test Fail
		PF7xx_FaultCodeList[84]	85	97	AutoTune Mag Cur Rotate Test Fail
		PF7xx_FaultCodeList[85]	86	98	AutoTune Saturation Curve Test Fail
		PF7xx_FaultCodeList[86]	87	99	User Set Timed Out
		PF7xx_FaultCodeList[87]	88	100	Parameter Checksum
		PF7xx_FaultCodeList[88]	89	101	UserSet1 Checksum
		PF7xx_FaultCodeList[89]	90	102	UserSet2 Checksum
		PF7xx_FaultCodeList[90]	91	103	UserSet3 Checksum
		PF7xx_FaultCodeList[91]	92	104	Power Board Checksum 1
		PF7xx_FaultCodeList[92]	93	105	Power Board Checksum 2
		PF7xx_FaultCodeList[93]	94	106	Incompat. MCB-PB
		PF7xx_FaultCodeList[94]	95	107	Replaced MCB-PB
		PF7xx_FaultCodeList[95]	96	108	Analog Cal Checksum
		PF7xx_FaultCodeList[96]	97	112	Power Down Checksum
		PF7xx_FaultCodeList[97]	98	113	Fatal Application Error
		PF7xx_FaultCodeList[98]	99	114	AutoTune Enabled but Not Started
		PF7xx_FaultCodeList[99]	100	120	I/O Board Replaced
		PF7xx_FaultCodeList[100]	101	130	Hardware Fault
		PF7xx_FaultCodeList[101]	102	131	Hardware Fault
		PF7xx_FaultCodeList[102]	103	133	Digital Input Conflict A
		PF7xx_FaultCodeList[103]	104	134	Digital Input Conflict B
		PF7xx_FaultCodeList[104]	105	135	Digital Input Conflict C
		PF7xx_FaultCodeList[105]	106	136	Bipolar Conflict
		PF7xx_FaultCodeList[106]	107	139	User Set Conflict
		PF7xx_FaultCodeList[107]	108	143	TB Man Ref Select Conflict
		PF7xx_FaultCodeList[108]	109	147	Starting at Powerup
		PF7xx_FaultCodeList[109]	110	148	Internal DB Regulator Overheated
		PF7xx_FaultCodeList[110]	111	149	Wake Timer is Timing
		PF7xx_FaultCodeList[111]	112	150	Sleep Configuration Error

## PF700S
	PF700S_FaultCodeList	Read From CLX:
		Send To CLX:
	Fault codes and text for
	PowerFlex 700S series drives	Description:		Fault Code	Description for given Fault Code
		Usage:		UDT	UDT
		Data Type:		DINT	STRING_40
			(Origin)	.	.
Unit	Tag Description	TagName	Instance	Code	Desc
		Default Values:	0	0	Check drive manual for this fault code
		PF700S_FaultCodeList[0]	1	0	Check drive manual for this fault code
		PF700S_FaultCodeList[1]	2	48	No Controlling Device
		PF700S_FaultCodeList[2]	3	49	DPI Loss Port 1
		PF700S_FaultCodeList[3]	4	50	DPI Loss Port 2
		PF700S_FaultCodeList[4]	5		DPI Loss Port 3
		PF700S_FaultCodeList[5]	6	52	DPI Loss Port 4
		PF700S_FaultCodeList[6]	7	53	DPI Loss Port 5
		PF700S_FaultCodeList[7]	8	54	DPI Loss Port 6
		PF700S_FaultCodeList[8]	9	55	Network Loss DPI Port 1
		PF700S_FaultCodeList[9]	10	56	Network Loss DPI Port 2
		PF700S_FaultCodeList[10]	11	57	Network Loss DPI Port 3
		PF700S_FaultCodeList[11]	12	58	Network Loss DPI Port 4
		PF700S_FaultCodeList[12]	13	59	Network Loss DPI Port 5
		PF700S_FaultCodeList[13]	14	60	Network Loss DPI Port 6
		PF700S_FaultCodeList[14]	15	9	SyncLink Communication Fault
		PF700S_FaultCodeList[15]	16	10	Drive Power Loss
		PF700S_FaultCodeList[16]	17	11	Motor Overload Tripped
		PF700S_FaultCodeList[17]	18	12	Motor Overload Pending
		PF700S_FaultCodeList[18]	19	27	Instantaneous Motor Overcurrent
		PF700S_FaultCodeList[19]	20	26	Ground Fault
		PF700S_FaultCodeList[20]	21	18	External Fault Input
		PF700S_FaultCodeList[21]	22	1	Absolute Overspeed Detected
		PF700S_FaultCodeList[22]	23	2	Vref Deceleration Failed
		PF700S_FaultCodeList[23]	24	3	Encoder 0 Loss
		PF700S_FaultCodeList[24]	25	4	Encoder 1 Loss
		PF700S_FaultCodeList[25]	26	5	Option Port 0 Loss
		PF700S_FaultCodeList[26]	27	6	Option Port 1 Loss
		PF700S_FaultCodeList[27]	28	13	Motor Stalled
		PF700S_FaultCodeList[28]	29	14	Inverter Overtemperature Pending
		PF700S_FaultCodeList[29]	30	15	Inverter Overtemperature Trip
		PF700S_FaultCodeList[30]	31	16	Inverter Overload Pending
		PF700S_FaultCodeList[31]	32	17	Inverter Overload Trip
		PF700S_FaultCodeList[32]	33	19	DSP Memory Error
		PF700S_FaultCodeList[33]	34	20	DSP Device Error
		PF700S_FaultCodeList[34]	35	21	Error Inertia Test
		PF700S_FaultCodeList[35]	36	22	Overfrequency Fault
		PF700S_FaultCodeList[36]	37	23	MC Commissioning Failed
		PF700S_FaultCodeList[37]	38	24	DC Bus Overvoltage
		PF700S_FaultCodeList[38]	39	28	VPL/MC Communication Fail
		PF700S_FaultCodeList[39]	40	29	PWM Signal Short
		PF700S_FaultCodeList[40]	41	30	MC Firmware Fault
		PF700S_FaultCodeList[41]	42	31	Precharge Error
		PF700S_FaultCodeList[42]	43	32	PWM Not Synchronized
		PF700S_FaultCodeList[43]	44	33	+/- 12V Power Fault
		PF700S_FaultCodeList[44]	45	35	Controller EEPROM Checksum
		PF700S_FaultCodeList[45]	46	38	Brake Overload Trip
		PF700S_FaultCodeList[46]	47	39	Power EEPROM CRC Failed
		PF700S_FaultCodeList[47]	48	40	SyncLink Multiplier Overflow
		PF700S_FaultCodeList[48]	49	41	Bus Loss Ridethru Timed Out
		PF700S_FaultCodeList[49]	50	42	DC Bus Undervoltage
		PF700S_FaultCodeList[50]	51	43	Voltage Feedback Loss
		PF700S_FaultCodeList[51]	52	44	Runtime Data were Reset
		PF700S_FaultCodeList[52]	53	46	Interpolator Out of Sync
		PF700S_FaultCodeList[53]	54	61	DriveLogix Taken Out of Run Mode
		PF700S_FaultCodeList[54]	55	62	DriveLogix Communication Timeout
		PF700S_FaultCodeList[55]	56	63	DriveLogix Connection Closed
		PF700S_FaultCodeList[56]	57	64	DriveLogix Comm Format Changed
		PF700S_FaultCodeList[57]	58	65	HiHP Drive: Input AC Phase Loss
		PF700S_FaultCodeList[58]	59	66	HiHP Drive: Bus Communication Delay
		PF700S_FaultCodeList[59]	60	67	HiHP Drive: Bus Comm Link Loss
		PF700S_FaultCodeList[60]	61	68	HiHP Drive: Bus CRC Error
		PF700S_FaultCodeList[61]	62	69	HiHP Drive: Bus Watchdog Timeout
		PF700S_FaultCodeList[62]	63	70	HiHP Drive: Fan Feedback Lost
		PF700S_FaultCodeList[63]	64	71	HiHP Drive: Overload
		PF700S_FaultCodeList[64]	65	72	HiHP Drive: Power Board Proc Error
		PF700S_FaultCodeList[65]	66	73	HiHP Drive: Precharge Contactor Fault
		PF700S_FaultCodeList[66]	67	74	HiHP Drive: Power EEPROM Error
		PF700S_FaultCodeList[67]	68	75	HiHP Drive: Power Board Overtemp
		PF700S_FaultCodeList[68]	69	85	Position Error

## PF75x
	PF75x_FaultCodeList	Read From CLX:
		Send To CLX:
	Fault codes and text for
	PowerFlex 750 series drives (753, 755)	Description:		Fault Code	Description for given Fault Code
		Usage:		UDT	UDT
		Data Type:		DINT	STRING_40
			(Origin)	.	.
Unit	Tag Description	TagName	Instance	Code	Desc
		Default Values:	0	0	Check drive manual for this fault code
		PF75x_FaultCodeList[0]	1	0	Check drive manual for this fault code
		PF75x_FaultCodeList[1]	2	13032	I/O Network Communication Fault
		PF75x_FaultCodeList[2]	3	13035	I/O Network Idle (Controller in PROG)
		PF75x_FaultCodeList[3]	4	13030	I/O Network Link Removed
		PF75x_FaultCodeList[4]	5		I/O Network Duplicate Address
		PF75x_FaultCodeList[5]	6	13033	I/O Network Sent Reset Command
		PF75x_FaultCodeList[6]	7	13034	I/O Network Connection Closed
		PF75x_FaultCodeList[7]	8	13037	I/O Network Timed Out
		PF75x_FaultCodeList[8]	9	13044	Control Network Message Timed Out
		PF75x_FaultCodeList[9]	10	13046	Peer-to-Peer I/O Timed Out
		PF75x_FaultCodeList[10]	11	13056	Drive Could Not Send e-mail
		PF75x_FaultCodeList[11]	12	13057	I/O Network Adapter Fault
		PF75x_FaultCodeList[12]	13	13058	I/O Network Adapter Set to Defaults
		PF75x_FaultCodeList[13]	14	2	Auxiliary Input Interlock
		PF75x_FaultCodeList[14]	15	3	Power Failure
		PF75x_FaultCodeList[15]	16	4	Bus Undervoltage
		PF75x_FaultCodeList[16]	17	5	Bus Overvoltage
		PF75x_FaultCodeList[17]	18	7	Motor Overload
		PF75x_FaultCodeList[18]	19	8	Heatsink Overtemperature
		PF75x_FaultCodeList[19]	20	9	Transistor Overtemperature
		PF75x_FaultCodeList[20]	21	10	Dynamic Brake Resistor Overtemperature
		PF75x_FaultCodeList[21]	22	12	Hardware Overcurrent
		PF75x_FaultCodeList[22]	23	13	Ground Fault
		PF75x_FaultCodeList[23]	24	14	Ground Warning
		PF75x_FaultCodeList[24]	25	15	Load Loss
		PF75x_FaultCodeList[25]	26	17	Input Phase Loss
		PF75x_FaultCodeList[26]	27	18	Motor Pos. Temp. Coeff. Trip
		PF75x_FaultCodeList[27]	28	20	Torque Prv. Speed Band Fault
		PF75x_FaultCodeList[28]	29	21	Output Phase Loss
		PF75x_FaultCodeList[29]	30	24	Deceleration Inhibited
		PF75x_FaultCodeList[30]	31	25	Over Speed Limit
		PF75x_FaultCodeList[31]	32	29	Analog Input Signal Loss
		PF75x_FaultCodeList[32]	33	33	Auto Restart Tries Exhausted
		PF75x_FaultCodeList[33]	34	36	Output Current Over Rating
		PF75x_FaultCodeList[34]	35	38	Phase U Ground Fault
		PF75x_FaultCodeList[35]	36	39	Phase V Ground Fault
		PF75x_FaultCodeList[36]	37	40	Phase W Ground Fault
		PF75x_FaultCodeList[37]	38	41	Phase U to V Shorted
		PF75x_FaultCodeList[38]	39	42	Phase V to W Shorted
		PF75x_FaultCodeList[39]	40	43	Phase W to U Shorted
		PF75x_FaultCodeList[40]	41	44	Phase U (Neg) Ground Fault
		PF75x_FaultCodeList[41]	42	45	Phase V (Neg) Ground Fault
		PF75x_FaultCodeList[42]	43	46	Phase W (Neg) Ground Fault
		PF75x_FaultCodeList[43]	44	48	Drive Set to Default Configuration
		PF75x_FaultCodeList[44]	45	55	Drive Control Board Overtemperature
		PF75x_FaultCodeList[45]	46	58	Drive Module Set to Default Values
		PF75x_FaultCodeList[46]	47	61	Shear Pin (1)
		PF75x_FaultCodeList[47]	48	62	Shear Pin (2)
		PF75x_FaultCodeList[48]	49	64	Drive OverLoad
		PF75x_FaultCodeList[49]	50	71	Port 1 Adapter Fault
		PF75x_FaultCodeList[50]	51	72	Port 2 Adapter Fault
		PF75x_FaultCodeList[51]	52	73	Port 3 Adapter Fault
		PF75x_FaultCodeList[52]	53	74	Port 4 Adapter Fault
		PF75x_FaultCodeList[53]	54	75	Port 5 Adapter Fault
		PF75x_FaultCodeList[54]	55	76	Port 6 Adapter Fault
		PF75x_FaultCodeList[55]	56	77	IR Volts Range
		PF75x_FaultCodeList[56]	57	78	Flux Amps Reference Rating
		PF75x_FaultCodeList[57]	58	79	Excessive Load
		PF75x_FaultCodeList[58]	59	80	Drive Autotune Aborted
		PF75x_FaultCodeList[59]	60	81	Port 1 DPI Communication Loss
		PF75x_FaultCodeList[60]	61	82	Port 2 DPI Communication Loss
		PF75x_FaultCodeList[61]	62	83	Port 3 DPI Communication Loss
		PF75x_FaultCodeList[62]	63	84	Port 4 DPI Communication Loss
		PF75x_FaultCodeList[63]	64	85	Port 5 DPI Communication Loss
		PF75x_FaultCodeList[64]	65	86	Port 6 DPI Communication Loss
		PF75x_FaultCodeList[65]	66	87	IXo Voltage Range
		PF75x_FaultCodeList[66]	67	91	Primary Velocity Feedback Lost
		PF75x_FaultCodeList[67]	68	93	Hardware Enable Jumper Problem
		PF75x_FaultCodeList[68]	69	94	Alternate Velocity Feedback Lost
		PF75x_FaultCodeList[69]	70	95	Auxiliary Velocity Feedback Lost
		PF75x_FaultCodeList[70]	71	96	Position Feedback Lost
		PF75x_FaultCodeList[71]	72	97	Auto Tach Switch Failure
		PF75x_FaultCodeList[72]	73	137	External Precharge Error
		PF75x_FaultCodeList[73]	74	138	Precharge Open
		PF75x_FaultCodeList[74]	75	152	No Source Defined for Stop Command
		PF75x_FaultCodeList[75]	76	168	Heatsink Undertemp (sensor fail)
		PF75x_FaultCodeList[76]	77	175	Travel Limits Conflicting
		PF75x_FaultCodeList[77]	78	181	Reached Forward End of Travel
		PF75x_FaultCodeList[78]	79	182	Reached Reverse End of Travel
		PF75x_FaultCodeList[79]	80	203	Port 13 Adapter (Ethernet) Fault
		PF75x_FaultCodeList[80]	81	204	Port 14 Adapter (DriveLogix) Fault
		PF75x_FaultCodeList[81]	82	210	Safety Option Enable Jumper is Out
		PF75x_FaultCodeList[82]	83	211	Safety Option Board Fault
		PF75x_FaultCodeList[83]	84	212	Safety Jumper Not Present
		PF75x_FaultCodeList[84]	85	213	Safety Jumper Needs Removed
		PF75x_FaultCodeList[85]	86	224	Port 4 Communication Lost
		PF75x_FaultCodeList[86]	87	225	Port 5 Communication Lost
		PF75x_FaultCodeList[87]	88	226	Port 6 Communication Lost
		PF75x_FaultCodeList[88]	89	227	Port 7 Communication Lost
		PF75x_FaultCodeList[89]	90	228	Port 8 Communication Lost
		PF75x_FaultCodeList[90]	91	229	Port 9 Communication Lost
		PF75x_FaultCodeList[91]	92	230	Port 10 Communication Lost
		PF75x_FaultCodeList[92]	93	231	Port 11 Communication Lost
		PF75x_FaultCodeList[93]	94	232	Port 12 Communication Lost
		PF75x_FaultCodeList[94]	95	233	Port 13 Communication Lost
		PF75x_FaultCodeList[95]	96	234	Port 14 Communication Lost
		PF75x_FaultCodeList[96]	97	315	Excess Position Error
		PF75x_FaultCodeList[97]	98	331	Inverter Board I1 Communication Failed
		PF75x_FaultCodeList[98]	99	332	Inverter Board I2 Communication Failed
		PF75x_FaultCodeList[99]	100	341	Converter Board C1 Communication Failed
		PF75x_FaultCodeList[100]	101	342	Converter Board C2 Communication Failed
		PF75x_FaultCodeList[101]	102	371	Precharge Board P1 Communication Failed
		PF75x_FaultCodeList[102]	103	372	Precharge Board P2 Communication Failed
		PF75x_FaultCodeList[103]	104	918	Control Task Overload
		PF75x_FaultCodeList[104]	105	919	System Task Overload
		PF75x_FaultCodeList[105]	106	920	5 millisecond Task Overload
		PF75x_FaultCodeList[106]	107	10101	Inverter I1 Communication Failed
		PF75x_FaultCodeList[107]	108	10104	Inverter I1 U+ Phase Overcurrent
		PF75x_FaultCodeList[108]	109	10105	Inverter I1 U- Phase Overcurrent
		PF75x_FaultCodeList[109]	110	10106	Inverter I1 V+ Phase Overcurrent
		PF75x_FaultCodeList[110]	111	10107	Inverter I1 V- Phase Overcurrent
		PF75x_FaultCodeList[111]	112	10108	Inverter I1 W+ Phase Overcurrent
		PF75x_FaultCodeList[112]	113	10109	Inverter I1 W- Phase Overcurrent
		PF75x_FaultCodeList[113]	114	10110	Inverter I1 Bus Overvoltage
		PF75x_FaultCodeList[114]	115	10111	Inverter I1 Ground Fault
		PF75x_FaultCodeList[115]	116	10112	Inverter I1 IGBT Overtemperature
		PF75x_FaultCodeList[116]	117	10113	Inverter I1 Heatsink Overtemperature
		PF75x_FaultCodeList[117]	118	10114	Inverter I1 Main Power Low
		PF75x_FaultCodeList[118]	119	10115	Inverter I1 Interface Power Low
		PF75x_FaultCodeList[119]	120	10117	Inverter I1 System Power Overcurrent
		PF75x_FaultCodeList[120]	121	10120	Inverter I1 PLI Board Overtemperature
		PF75x_FaultCodeList[121]	122	10121	Inverter I1 PS Board Overtemperature
		PF75x_FaultCodeList[122]	123	10129	Inverter I1 DC Bus Imbalance
		PF75x_FaultCodeList[123]	124	10134	Inverter I1 Phase U Gate Board Fault
		PF75x_FaultCodeList[124]	125	10135	Inverter I1 Phase V Gate Board Fault
		PF75x_FaultCodeList[125]	126	10136	Inverter I1 Phase W Gate Board Fault
		PF75x_FaultCodeList[126]	127	10201	Inverter I2 Communication Failed
		PF75x_FaultCodeList[127]	128	10204	Inverter I2 U+ Phase Overcurrent
		PF75x_FaultCodeList[128]	129	10205	Inverter I2 U- Phase Overcurrent
		PF75x_FaultCodeList[129]	130	10206	Inverter I2 V+ Phase Overcurrent
		PF75x_FaultCodeList[130]	131	10207	Inverter I2 V- Phase Overcurrent
		PF75x_FaultCodeList[131]	132	10208	Inverter I2 W+ Phase Overcurrent
		PF75x_FaultCodeList[132]	133	10209	Inverter I2 W- Phase Overcurrent
		PF75x_FaultCodeList[133]	134	10210	Inverter I2 Bus Overvoltage
		PF75x_FaultCodeList[134]	135	10211	Inverter I2 Ground Fault
		PF75x_FaultCodeList[135]	136	10212	Inverter I2 IGBT Overtemperature
		PF75x_FaultCodeList[136]	137	10213	Inverter I2 Heatsink Overtemperature
		PF75x_FaultCodeList[137]	138	10214	Inverter I2 Main Power Low
		PF75x_FaultCodeList[138]	139	10215	Inverter I2 Interface Power Low
		PF75x_FaultCodeList[139]	140	10217	Inverter I2 System Power Overcurrent
		PF75x_FaultCodeList[140]	141	10220	Inverter I2 PLI Board Overtemperature
		PF75x_FaultCodeList[141]	142	10221	Inverter I2 PS Board Overtemperature
		PF75x_FaultCodeList[142]	143	10229	Inverter I2 DC Bus Imbalance
		PF75x_FaultCodeList[143]	144	10234	Inverter I2 Phase U Gate Board Fault
		PF75x_FaultCodeList[144]	145	10235	Inverter I2 Phase V Gate Board Fault
		PF75x_FaultCodeList[145]	146	10236	Inverter I2 Phase W Gate Board Fault
		PF75x_FaultCodeList[146]	147	10301	Inverter I3 Communication Failed
		PF75x_FaultCodeList[147]	148	10304	Inverter I3 U+ Phase Overcurrent
		PF75x_FaultCodeList[148]	149	10305	Inverter I3 U- Phase Overcurrent
		PF75x_FaultCodeList[149]	150	10306	Inverter I3 V+ Phase Overcurrent
		PF75x_FaultCodeList[150]	151	10307	Inverter I3 V- Phase Overcurrent
		PF75x_FaultCodeList[151]	152	10308	Inverter I3 W+ Phase Overcurrent
		PF75x_FaultCodeList[152]	153	10309	Inverter I3 W- Phase Overcurrent
		PF75x_FaultCodeList[153]	154	10310	Inverter I3 Bus Overvoltage
		PF75x_FaultCodeList[154]	155	10311	Inverter I3 Ground Fault
		PF75x_FaultCodeList[155]	156	10312	Inverter I3 IGBT Overtemperature
		PF75x_FaultCodeList[156]	157	10313	Inverter I3 Heatsink Overtemperature
		PF75x_FaultCodeList[157]	158	10314	Inverter I3 Main Power Low
		PF75x_FaultCodeList[158]	159	10315	Inverter I3 Interface Power Low
		PF75x_FaultCodeList[159]	160	10317	Inverter I3 System Power Overcurrent
		PF75x_FaultCodeList[160]	161	10320	Inverter I3 PLI Board Overtemperature
		PF75x_FaultCodeList[161]	162	10321	Inverter I3 PS Board Overtemperature
		PF75x_FaultCodeList[162]	163	10329	Inverter I3 DC Bus Imbalance
		PF75x_FaultCodeList[163]	164	10334	Inverter I3 Phase U Gate Board Fault
		PF75x_FaultCodeList[164]	165	10335	Inverter I3 Phase V Gate Board Fault
		PF75x_FaultCodeList[165]	166	10336	Inverter I3 Phase W Gate Board Fault
		PF75x_FaultCodeList[166]	167	11101	Converter C1 Precharge Problem
		PF75x_FaultCodeList[167]	168	11111	Converter C1 SCR Overtemperature
		PF75x_FaultCodeList[168]	169	11112	Converter C1 Heat Sink Overtemp
		PF75x_FaultCodeList[169]	170	11115	Converter C1 Line/Bus Voltage Dip
		PF75x_FaultCodeList[170]	171	11117	Converter C1 Line Frequency Fault
		PF75x_FaultCodeList[171]	172	11118	Converter C1 Single Phase Fault
		PF75x_FaultCodeList[172]	173	11134	Converter C1 Overcurrent
		PF75x_FaultCodeList[173]	174	11135	Converter C1 Ground Fault
		PF75x_FaultCodeList[174]	175	11138	Converter C1 Board Overtemperature
		PF75x_FaultCodeList[175]	176	11141	Converter C1 DC Power Supply Fault
		PF75x_FaultCodeList[176]	177	11142	Converter C1 Communication Lost
		PF75x_FaultCodeList[177]	178	11160	Converter C1 Bus Asymmetry Stop
		PF75x_FaultCodeList[178]	179	11161	Converter C1 AC Line Overvoltage
		PF75x_FaultCodeList[179]	180	11162	Converter C1 AC Line Lost
		PF75x_FaultCodeList[180]	181	11163	Converter C1 Fault Queue Full
		PF75x_FaultCodeList[181]	182	11201	Converter C2 Precharge Problem
		PF75x_FaultCodeList[182]	183	11211	Converter C2 SCR Overtemperature
		PF75x_FaultCodeList[183]	184	11212	Converter C2 Heat Sink Overtemp
		PF75x_FaultCodeList[184]	185	11215	Converter C2 Line/Bus Voltage Dip
		PF75x_FaultCodeList[185]	186	11217	Converter C2 Line Frequency Fault
		PF75x_FaultCodeList[186]	187	11218	Converter C2 Single Phase Fault
		PF75x_FaultCodeList[187]	188	11234	Converter C2 Overcurrent
		PF75x_FaultCodeList[188]	189	11235	Converter C2 Ground Fault
		PF75x_FaultCodeList[189]	190	11238	Converter C2 Board Overtemperature
		PF75x_FaultCodeList[190]	191	11241	Converter C2 DC Power Supply Fault
		PF75x_FaultCodeList[191]	192	11242	Converter C2 Communication Lost
		PF75x_FaultCodeList[192]	193	11260	Converter C2 Bus Asymmetry Stop
		PF75x_FaultCodeList[193]	194	11261	Converter C2 AC Line Overvoltage
		PF75x_FaultCodeList[194]	195	11262	Converter C2 AC Line Lost
		PF75x_FaultCodeList[195]	196	11263	Converter C2 Fault Queue Full
		PF75x_FaultCodeList[196]	197	11201	Converter C2 Precharge Problem
		PF75x_FaultCodeList[197]	198	11211	Converter C2 SCR Overtemperature
		PF75x_FaultCodeList[198]	199	11212	Converter C2 Heat Sink Overtemp
		PF75x_FaultCodeList[199]	200	11215	Converter C2 Line/Bus Voltage Dip
		PF75x_FaultCodeList[200]	201	11217	Converter C2 Line Frequency Fault
		PF75x_FaultCodeList[201]	202	11218	Converter C2 Single Phase Fault
		PF75x_FaultCodeList[202]	203	11234	Converter C2 Overcurrent
		PF75x_FaultCodeList[203]	204	11235	Converter C2 Ground Fault
		PF75x_FaultCodeList[204]	205	11238	Converter C2 Board Overtemperature
		PF75x_FaultCodeList[205]	206	11241	Converter C2 DC Power Supply Fault
		PF75x_FaultCodeList[206]	207	11242	Converter C2 Communication Lost
		PF75x_FaultCodeList[207]	208	11260	Converter C2 Bus Asymmetry Stop
		PF75x_FaultCodeList[208]	209	11261	Converter C2 AC Line Overvoltage
		PF75x_FaultCodeList[209]	210	11262	Converter C2 AC Line Lost
		PF75x_FaultCodeList[210]	211	11263	Converter C2 Fault Queue Full

## PFDC
	PFDC_FaultCodeList	Read From CLX:
		Send To CLX:
	Fault codes and text for
	PowerFlex DC series drives	Description:		Fault Code	Description for given Fault Code
		Usage:		UDT	UDT
		Data Type:		DINT	STRING_40
			(Origin)	.	.
Unit	Tag Description	TagName	Instance	Code	Desc
		Default Values:	0	0	Check drive manual for this fault code
		PFDC_FaultCodeList[0]	1	0	Check drive manual for this fault code
		PFDC_FaultCodeList[1]	2	71	Port 1 Adapter
		PFDC_FaultCodeList[2]	3	72	Port 2 Adapter
		PFDC_FaultCodeList[3]	4	73	Port 3 Adapter
		PFDC_FaultCodeList[4]	5		Port 4 Adapter
		PFDC_FaultCodeList[5]	6	75	Port 5 Adapter
		PFDC_FaultCodeList[6]	7	81	Port 1 DPI Loss
		PFDC_FaultCodeList[7]	8	82	Port 2 DPI Loss
		PFDC_FaultCodeList[8]	9	83	Port 3 DPI Loss
		PFDC_FaultCodeList[9]	10	84	Port 4 DPI Loss
		PFDC_FaultCodeList[10]	11	85	Port 5 DPI Loss
		PFDC_FaultCodeList[11]	12	2	Auxiliary Input
		PFDC_FaultCodeList[12]	13	3	Power Failure
		PFDC_FaultCodeList[13]	14	4	AC Undervoltage
		PFDC_FaultCodeList[14]	15	5	Arm Overvoltage
		PFDC_FaultCodeList[15]	16	6	Field Current Loss
		PFDC_FaultCodeList[16]	17	7	Motor Overload
		PFDC_FaultCodeList[17]	18	8	Heatsink Overtemp
		PFDC_FaultCodeList[18]	19	10	Main Contactor
		PFDC_FaultCodeList[19]	20	13	Overcurrent
		PFDC_FaultCodeList[20]	21	16	Motor Overtemp
		PFDC_FaultCodeList[21]	22	25	Overspeed
		PFDC_FaultCodeList[22]	23	37	Inverting Fault
		PFDC_FaultCodeList[23]	24	48	Parameters Defaulted
		PFDC_FaultCodeList[24]	25	56	STune Overspeed
		PFDC_FaultCodeList[25]	26	57	STune Stalled
		PFDC_FaultCodeList[26]	27	58	STune Load Hi
		PFDC_FaultCodeList[27]	28	59	STune Current Limit
		PFDC_FaultCodeList[28]	29	60	STune Friction Lo
		PFDC_FaultCodeList[29]	30	61	STune Timeout
		PFDC_FaultCodeList[30]	31	62	STune Aborted
		PFDC_FaultCodeList[31]	32	64	Drive Overload
		PFDC_FaultCodeList[32]	33	70	Sustained Current
		PFDC_FaultCodeList[33]	34	91	Speed Fdbk Loss
		PFDC_FaultCodeList[34]	35	92	Encoder Error
		PFDC_FaultCodeList[35]	36	93	Resolver Error
		PFDC_FaultCodeList[36]	37	100	EEPROM Error
		PFDC_FaultCodeList[37]	38	130	Hardware Fault
		PFDC_FaultCodeList[38]	39	131	Interrupt Error
		PFDC_FaultCodeList[39]	40	132	DSP Error

## SMC50
	SMC50_FaultCodeList	Read From CLX:
		Send To CLX:
	Fault codes and text for
	SMC-50 Smart Motor Controllers	Description:		Fault Code	Description for given Trip Code
		Usage:		UDT	UDT
		Data Type:		DINT	STRING_40
			(Origin)	.	.
Unit	Tag Description	TagName	Instance	Code	Desc
		Default Values:	0	0	Check starter manual for this fault code
		SMC50_FaultCodeList[0]	1	0	Check starter manual for this fault code
		SMC50_FaultCodeList[1]	2	1	Line Loss Phase A
		SMC50_FaultCodeList[2]	3	2	Line Loss Phase B
		SMC50_FaultCodeList[3]	4	3	Line Loss Phase C
		SMC50_FaultCodeList[4]	5		Shorted SCR Phase A
		SMC50_FaultCodeList[5]	6	5	Shorted SCR Phase B
		SMC50_FaultCodeList[6]	7	6	Shorted SCR Phase C
		SMC50_FaultCodeList[7]	8	7	Open SCR Gate Phase A
		SMC50_FaultCodeList[8]	9	8	Open SCR Gate Phase B
		SMC50_FaultCodeList[9]	10	9	Open SCR Gate Phase C
		SMC50_FaultCodeList[10]	11	10	SMC-50 SCR Overtemperature
		SMC50_FaultCodeList[11]	12	14	No Load or Load Connection Failed
		SMC50_FaultCodeList[12]	13	15	Open Load Circuit Phase A
		SMC50_FaultCodeList[13]	14	16	Open Load Circuit Phase B
		SMC50_FaultCodeList[14]	15	17	Open Load Circuit Phase C
		SMC50_FaultCodeList[15]	16	18	Voltage Imbalance
		SMC50_FaultCodeList[16]	17	19	Line Overvoltage
		SMC50_FaultCodeList[17]	18	20	Line Undervoltage
		SMC50_FaultCodeList[18]	19	21	Motor Overload Trip
		SMC50_FaultCodeList[19]	20	22	Motor Underload Trip
		SMC50_FaultCodeList[20]	21	23	Motor / Shaft / Part Jam Trip
		SMC50_FaultCodeList[21]	22	24	Motor Stall Trip
		SMC50_FaultCodeList[22]	23	25	Incoming Power Phase Reversal
		SMC50_FaultCodeList[23]	24	26	Required Expansion Module Removed
		SMC50_FaultCodeList[24]	25	27	Expansion Module Is Incompatible
		SMC50_FaultCodeList[25]	26	28	Expansion Module or Peripheral Fault
		SMC50_FaultCodeList[26]	27	29	Too many motor starts in the last hour
		SMC50_FaultCodeList[27]	28	30	Current Transformer Loss Phase A
		SMC50_FaultCodeList[28]	29	31	Current Transformer Loss Phase B
		SMC50_FaultCodeList[29]	30	32	Current Transformer Loss Phase C
		SMC50_FaultCodeList[30]	31	33	HAL ID Fault (Incompatible Power Pole)
		SMC50_FaultCodeList[31]	32	34	Nonvolatile (FLASH) Memory Fault
		SMC50_FaultCodeList[32]	33	36	24 VDC Control Power Supply Failure
		SMC50_FaultCodeList[33]	34	37	Control Voltage Out of Specification
		SMC50_FaultCodeList[34]	35	38	Configurable Fault Input #1 Triggered
		SMC50_FaultCodeList[35]	36	39	Configurable Fault Input #2 Triggered
		SMC50_FaultCodeList[36]	37	40	Configurable Fault Input #3 Triggered
		SMC50_FaultCodeList[37]	38	41	Configurable Fault Input #4 Triggered
		SMC50_FaultCodeList[38]	39	42	High Motor Current Imbalance
		SMC50_FaultCodeList[39]	40	43	Real Power Below Configured Low Limit
		SMC50_FaultCodeList[40]	41	44	Real Power Above Configured High Limit
		SMC50_FaultCodeList[41]	42	45	Reactive Power Below Configured Lo Limit
		SMC50_FaultCodeList[42]	43	46	Reactive Power Above Configured Hi Limit
		SMC50_FaultCodeList[43]	44	47	Apparent Power Below Configured Lo Limit
		SMC50_FaultCodeList[44]	45	48	Apparent Power Above Configured Hi Limit
		SMC50_FaultCodeList[45]	46	49	Power Line Frequency Out of Spec
		SMC50_FaultCodeList[46]	47	50	Total Run Hours: PM is Required
		SMC50_FaultCodeList[47]	48	51	Total Motor Starts: PM is Required
		SMC50_FaultCodeList[48]	49	52	SCR Phase A Power Quality / Firing Fault
		SMC50_FaultCodeList[49]	50	53	SCR Phase B Power Quality / Firing Fault
		SMC50_FaultCodeList[50]	51	54	SCR Phase C Power Quality / Firing Fault
		SMC50_FaultCodeList[51]	52	55	Power Quality V THD Out of Spec
		SMC50_FaultCodeList[52]	53	56	Power Quality I THD Out of Spec
		SMC50_FaultCodeList[53]	54	57	Configuration Changed
		SMC50_FaultCodeList[54]	55	58	Excessive Ground Fault Current
		SMC50_FaultCodeList[55]	56	59	Motor Overtemperature (from sensor)
		SMC50_FaultCodeList[56]	57	60	Power Pole Overtemperature (from sensor)
		SMC50_FaultCodeList[57]	58	61	SMC-50 I/O Configuration Fault
		SMC50_FaultCodeList[58]	59	62	Push-to-Test (Test Trip) Fault
		SMC50_FaultCodeList[59]	60	63	Lagging Power Factor below fault limit
		SMC50_FaultCodeList[60]	61	64	Leading Power Factor below fault limit
		SMC50_FaultCodeList[61]	62	65	Lagging Power Factor above fault limit
		SMC50_FaultCodeList[62]	63	66	Leading Power Factor above fault limit
		SMC50_FaultCodeList[63]	64	67	MVAR (Reactive Power) above fault limit
		SMC50_FaultCodeList[64]	65	68	MVAR (Reactive Power) below fault limit
		SMC50_FaultCodeList[65]	66	69	Replace SMC-50 Real-Time Clock Battery
		SMC50_FaultCodeList[66]	67	70	Motor Locked Rotor fault

## SMCFlex
	SMCFlex_FaultCodeList	Read From CLX:
		Send To CLX:
	Fault codes and text for
	SMCFlex Smart Motor Controllers	Description:		Fault Code	Description for given Warning Code
		Usage:		UDT	UDT
		Data Type:		DINT	STRING_40
			(Origin)	.	.
Unit	Tag Description	TagName	Instance	Code	Desc
		Default Values:	0	0	Check starter manual for this fault code
		SMCFlex_FaultCodeList[0]	1	0	Check starter manual for this fault code
		SMCFlex_FaultCodeList[1]	2	1	Fault: Phase A Power / Line Lost
		SMCFlex_FaultCodeList[2]	3	2	Fault: Phase B Power / Line Lost
		SMCFlex_FaultCodeList[3]	4	3	Fault: Phase C Power / Line Lost
		SMCFlex_FaultCodeList[4]	5		Fault: Shorted SCR for Phase A
		SMCFlex_FaultCodeList[5]	6	5	Fault: Shorted SCR for Phase B
		SMCFlex_FaultCodeList[6]	7	6	Fault: Shorted SCR for Phase C
		SMCFlex_FaultCodeList[7]	8	7	Fault: Open Gate on SCR for Phase A
		SMCFlex_FaultCodeList[8]	9	8	Fault: Open Gate on SCR for Phase B
		SMCFlex_FaultCodeList[9]	10	9	Fault: Open Gate on SCR for Phase C
		SMCFlex_FaultCodeList[10]	11	10	PTC (Temp Sensor) Power Pole Fault
		SMCFlex_FaultCodeList[11]	12	11	SMCFlex SCR Overtemperature Fault
		SMCFlex_FaultCodeList[12]	13	12	Motor Overtemperature Fault (or bad PTC)
		SMCFlex_FaultCodeList[13]	14	13	Open Bypass Fault on Phase A
		SMCFlex_FaultCodeList[14]	15	14	Open Bypass Fault on Phase B
		SMCFlex_FaultCodeList[15]	16	15	Open Bypass Fault on Phase C
		SMCFlex_FaultCodeList[16]	17	16	No Load on Phase A (broken wire?)
		SMCFlex_FaultCodeList[17]	18	17	No Load on Phase B (broken wire?)
		SMCFlex_FaultCodeList[18]	19	18	No Load on Phase C (broken wire?)
		SMCFlex_FaultCodeList[19]	20	19	Line Unbalance Fault
		SMCFlex_FaultCodeList[20]	21	20	Overvoltage Fault
		SMCFlex_FaultCodeList[21]	22	21	Undervoltage Fault
		SMCFlex_FaultCodeList[22]	23	22	Motor Overload Fault
		SMCFlex_FaultCodeList[23]	24	23	Underload Fault (broken shaft?)
		SMCFlex_FaultCodeList[24]	25	24	Jam Fault (Motor / Machine Stuck)
		SMCFlex_FaultCodeList[25]	26	25	Stalled Motor Fault
		SMCFlex_FaultCodeList[26]	27	26	Phase Reversal Fault
		SMCFlex_FaultCodeList[27]	28	27	Comms Lost on Network Port 2 (HIM, etc.)
		SMCFlex_FaultCodeList[28]	29	28	Comms Lost on Network Port 3 (HIM, etc.)
		SMCFlex_FaultCodeList[29]	30	29	Comms Lost on Network Port 5 (Ethernet)
		SMCFlex_FaultCodeList[30]	31	30	Network Port 2 Fault (HIM, etc.)
		SMCFlex_FaultCodeList[31]	32	31	Network Port 3 Fault (HIM, etc.)
		SMCFlex_FaultCodeList[32]	33	32	Net Port 5 Fault (Controller Comms/PROG)
		SMCFlex_FaultCodeList[33]	34	33	Ground Fault
		SMCFlex_FaultCodeList[34]	35	34	Starting too frequently
		SMCFlex_FaultCodeList[35]	36	35	Phase A Power Lost
		SMCFlex_FaultCodeList[36]	37	36	Phase B Power Lost
		SMCFlex_FaultCodeList[37]	38	37	Phase C Power Lost
		SMCFlex_FaultCodeList[38]	39	38	Hall Effect Sensor ID Fault
		SMCFlex_FaultCodeList[39]	40	39	Nonvolatile Memory Error
		SMCFlex_FaultCodeList[40]	41	40	Fault: No Load
		SMCFlex_FaultCodeList[41]	42	41	Phase A Line Lost
		SMCFlex_FaultCodeList[42]	43	42	Phase B Line Lost
		SMCFlex_FaultCodeList[43]	44	43	Phase C Line Lost
		SMCFlex_FaultCodeList[44]	45	45	24 Volt Supply Lost
		SMCFlex_FaultCodeList[45]	46	46	Voltage Control Lost
		SMCFlex_FaultCodeList[46]	47	48	Input 1 Fault
		SMCFlex_FaultCodeList[47]	48	49	Input 2 Fault

## P_LLS_Motors
	P_LLS_Motors: Group of Motors for P_LLS	Read From CLX:
		Send To CLX:
	Data for Interface Table for one motor Group
		Description:		Motor priority in list (0 to 31 -- if unused, set to 0)	Motor preference in list (0 to 31), all else being equal	Logix Tag to navigate to for this motor (e.g., P_Motor backing tag name)
	Copy and paste this sheet, modify tags,	Usage:		UDT	UDT	UDT
	and add to Setup sheet for each group.	Data Type:		DINT	DINT	STRING_20
			(Origin)	.Cfg_	.Cfg_	.Cfg_
Unit	Tag Description	TagName	Instance	Prio	Pref	NavTag
		Default Values:	0	0	0	0
	First Motor (<Ref_Motors_tag>[0])	MyP_LLS_Motors[0]	1	0	0	MyP_LLS_Motor01
		MyP_LLS_Motors[1]	2	0	0	MyP_LLS_Motor02
	Default = 3 motors, go to Setup Tab to change	MyP_LLS_Motors[2]	3	0	0	MyP_LLS_Motor03
		MyP_LLS_Motors[3]	4	0	0
		MyP_LLS_Motors[4]	5		0
		MyP_LLS_Motors[5]	6	0	0
		MyP_LLS_Motors[6]	7	0	0
		MyP_LLS_Motors[7]	8	0	0
		MyP_LLS_Motors[8]	9	0	0
		MyP_LLS_Motors[9]	10	0	0
		MyP_LLS_Motors[10]	11	0	0
		MyP_LLS_Motors[11]	12	0	0
		MyP_LLS_Motors[12]	13	0	0
		MyP_LLS_Motors[13]	14	0	0
		MyP_LLS_Motors[14]	15	0	0
		MyP_LLS_Motors[15]	16	0	0
		MyP_LLS_Motors[16]	17	0	0
		MyP_LLS_Motors[17]	18	0	0
		MyP_LLS_Motors[18]	19	0	0
		MyP_LLS_Motors[19]	20	0	0
		MyP_LLS_Motors[20]	21	0	0
		MyP_LLS_Motors[21]	22	0	0
		MyP_LLS_Motors[22]	23	0	0
		MyP_LLS_Motors[23]	24	0	0
		MyP_LLS_Motors[24]	25	0	0
		MyP_LLS_Motors[25]	26	0	0
		MyP_LLS_Motors[26]	27	0	0
		MyP_LLS_Motors[27]	28	0	0
		MyP_LLS_Motors[28]	29	0	0
	(Up to 30 Motors in a group)	MyP_LLS_Motors[29]	30	0	0

## P_StrapTblCfg
	P_StrapTblCfg: Strapping Table Config.	Read From CLX:
		Send To CLX:
	Data for Calibration Table for one tank
		Description:		Level Major Units (e.g., Feet)	Level Minor Runits (e.g., Inches)	Tank Volume (e.g., Bbl or Gal) at given Level
	Copy and paste this sheet, modify tags,	Usage:		UDT	UDT	UDT
	and add to Setup sheet for each tank.	Data Type:		REAL	REAL	REAL
			(Origin)	.	.	.
Unit	Tag Description	TagName	Instance	Major	Minor	Volume
		Default Values:	0	0	0	0
		MyP_StrapTbl_CalTable[0]	1	0	0	327.3
		MyP_StrapTbl_CalTable[1]	2	0	1	662.9
		MyP_StrapTbl_CalTable[2]	3	0	2	1227.8
		MyP_StrapTbl_CalTable[3]	4	0	3	2006.1
		MyP_StrapTbl_CalTable[4]	5		4	2887.5
		MyP_StrapTbl_CalTable[5]	6	0	5	3771.1
		MyP_StrapTbl_CalTable[6]	7	0	6	4654.7
		MyP_StrapTbl_CalTable[7]	8	0	7	5538.2
		MyP_StrapTbl_CalTable[8]	9	0	8	6421.8
		MyP_StrapTbl_CalTable[9]	10	0	9	7305.4
		MyP_StrapTbl_CalTable[10]	11	0	10	8189.0
		MyP_StrapTbl_CalTable[11]	12	0	11	9072.6
		MyP_StrapTbl_CalTable[12]	13	1	0	9956.2
		MyP_StrapTbl_CalTable[13]	14	1	1	10839.8
		MyP_StrapTbl_CalTable[14]	15	1	2	11723.4
		MyP_StrapTbl_CalTable[15]	16	1	3	12607.0
		MyP_StrapTbl_CalTable[16]	17	1	4	13490.6
		MyP_StrapTbl_CalTable[17]	18	1	5	14374.2
		MyP_StrapTbl_CalTable[18]	19	1	6	15257.8
		MyP_StrapTbl_CalTable[19]	20	1	7	16141.4
		MyP_StrapTbl_CalTable[20]	21	1	8	17025.0
		MyP_StrapTbl_CalTable[21]	22	1	9	17908.6
		MyP_StrapTbl_CalTable[22]	23	1	10	18792.2
		MyP_StrapTbl_CalTable[23]	24	1	11	19675.8
		MyP_StrapTbl_CalTable[24]	25	2	0	20559.4
		MyP_StrapTbl_CalTable[25]	26	2	1	21443.0
		MyP_StrapTbl_CalTable[26]	27	2	2	22326.6
		MyP_StrapTbl_CalTable[27]	28	2	3	23210.2
		MyP_StrapTbl_CalTable[28]	29	2	4	24093.8
		MyP_StrapTbl_CalTable[29]	30	2	5	24977.4
		MyP_StrapTbl_CalTable[30]	31	2	6	25861.0
		MyP_StrapTbl_CalTable[31]	32	2	7	26744.6
		MyP_StrapTbl_CalTable[32]	33	2	8	27628.2
		MyP_StrapTbl_CalTable[33]	34	2	9	28511.8
		MyP_StrapTbl_CalTable[34]	35	2	10	29395.4
		MyP_StrapTbl_CalTable[35]	36	2	11	30279.0
		MyP_StrapTbl_CalTable[36]	37	3	0	31162.6
		MyP_StrapTbl_CalTable[37]	38	3	1	32046.2
		MyP_StrapTbl_CalTable[38]	39	3	2	32929.8
		MyP_StrapTbl_CalTable[39]	40	3	3	33813.4
		MyP_StrapTbl_CalTable[40]	41	3	4	34697.0
		MyP_StrapTbl_CalTable[41]	42	3	5	35580.6
		MyP_StrapTbl_CalTable[42]	43	3	6	36464.2
		MyP_StrapTbl_CalTable[43]	44	3	7	37347.8
		MyP_StrapTbl_CalTable[44]	45	3	8	38231.4
		MyP_StrapTbl_CalTable[45]	46	3	9	39115.0
		MyP_StrapTbl_CalTable[46]	47	3	10	39998.6
		MyP_StrapTbl_CalTable[47]	48	3	11	40882.2
		MyP_StrapTbl_CalTable[48]	49	4	0	41765.8
		MyP_StrapTbl_CalTable[49]	50	4	1	42648.2
		MyP_StrapTbl_CalTable[50]	51	4	2	43473.3
		MyP_StrapTbl_CalTable[51]	52	4	3	44256.9
		MyP_StrapTbl_CalTable[52]	53	4	4	45021.4
		MyP_StrapTbl_CalTable[53]	54	4	5	45777.2
		MyP_StrapTbl_CalTable[54]	55	4	6	46660.8
		MyP_StrapTbl_CalTable[55]	56	4	7	47544.4
		MyP_StrapTbl_CalTable[56]	57	4	8	48428.0
		MyP_StrapTbl_CalTable[57]	58	4	9	49311.6
		MyP_StrapTbl_CalTable[58]	59	4	10	50195.2
		MyP_StrapTbl_CalTable[59]	60	4	11	51078.8
		MyP_StrapTbl_CalTable[60]	61	5	0	51962.4
		MyP_StrapTbl_CalTable[61]	62	5	1	52845.9
		MyP_StrapTbl_CalTable[62]	63	5	2	53729.5
		MyP_StrapTbl_CalTable[63]	64	5	3	54613.1
		MyP_StrapTbl_CalTable[64]	65	5	4	55496.7
		MyP_StrapTbl_CalTable[65]	66	5	5	56380.2
		MyP_StrapTbl_CalTable[66]	67	5	6	57263.8
		MyP_StrapTbl_CalTable[67]	68	5	7	58147.4
		MyP_StrapTbl_CalTable[68]	69	5	8	59030.9
		MyP_StrapTbl_CalTable[69]	70	5	9	59914.5
		MyP_StrapTbl_CalTable[70]	71	5	10	60798.1
		MyP_StrapTbl_CalTable[71]	72	5	11	61681.7
		MyP_StrapTbl_CalTable[72]	73	6	0	62565.2
		MyP_StrapTbl_CalTable[73]	74	6	1	63448.8
		MyP_StrapTbl_CalTable[74]	75	6	2	64332.4
		MyP_StrapTbl_CalTable[75]	76	6	3	65215.9
		MyP_StrapTbl_CalTable[76]	77	6	4	66099.5
		MyP_StrapTbl_CalTable[77]	78	6	5	66983.1
		MyP_StrapTbl_CalTable[78]	79	6	6	67866.7
		MyP_StrapTbl_CalTable[79]	80	6	7	68750.2
		MyP_StrapTbl_CalTable[80]	81	6	8	69633.8
		MyP_StrapTbl_CalTable[81]	82	6	9	70517.4
		MyP_StrapTbl_CalTable[82]	83	6	10	71400.9
		MyP_StrapTbl_CalTable[83]	84	6	11	72284.5
		MyP_StrapTbl_CalTable[84]	85	7	0	73168.1
		MyP_StrapTbl_CalTable[85]	86	7	1	74051.7
		MyP_StrapTbl_CalTable[86]	87	7	2	74935.3
		MyP_StrapTbl_CalTable[87]	88	7	3	75818.9
		MyP_StrapTbl_CalTable[88]	89	7	4	76702.5
		MyP_StrapTbl_CalTable[89]	90	7	5	77586.1
		MyP_StrapTbl_CalTable[90]	91	7	6	78469.7
		MyP_StrapTbl_CalTable[91]	92	7	7	79353.3
		MyP_StrapTbl_CalTable[92]	93	7	8	80236.9
		MyP_StrapTbl_CalTable[93]	94	7	9	81119.7
		MyP_StrapTbl_CalTable[94]	95	7	10	82002.5
		MyP_StrapTbl_CalTable[95]	96	7	11	82885.3
		MyP_StrapTbl_CalTable[96]	97	8	0	83768.1
		MyP_StrapTbl_CalTable[97]	98	8	1	84650.9
		MyP_StrapTbl_CalTable[98]	99	8	2	85533.7
		MyP_StrapTbl_CalTable[99]	100	8	3	86416.5
		MyP_StrapTbl_CalTable[100]	101	8	4	87299.3
		MyP_StrapTbl_CalTable[101]	102	8	5	88182.1
		MyP_StrapTbl_CalTable[102]	103	8	6	89064.9
		MyP_StrapTbl_CalTable[103]	104	8	7	89947.7
		MyP_StrapTbl_CalTable[104]	105	8	8	90830.5
		MyP_StrapTbl_CalTable[105]	106	8	9	91713.3
		MyP_StrapTbl_CalTable[106]	107	8	10	92596.1
		MyP_StrapTbl_CalTable[107]	108	8	11	93478.9
		MyP_StrapTbl_CalTable[108]	109	9	0	94361.7
		MyP_StrapTbl_CalTable[109]	110	9	1	95244.5
		MyP_StrapTbl_CalTable[110]	111	9	2	96127.3
		MyP_StrapTbl_CalTable[111]	112	9	3	97010.1
		MyP_StrapTbl_CalTable[112]	113	9	4	97892.9
		MyP_StrapTbl_CalTable[113]	114	9	5	98775.7
		MyP_StrapTbl_CalTable[114]	115	9	6	99658.5
		MyP_StrapTbl_CalTable[115]	116	9	7	100541.3
		MyP_StrapTbl_CalTable[116]	117	9	8	101424.1
		MyP_StrapTbl_CalTable[117]	118	9	9	102306.9
		MyP_StrapTbl_CalTable[118]	119	9	10	103189.7
		MyP_StrapTbl_CalTable[119]	120	9	11	104072.5
		MyP_StrapTbl_CalTable[120]	121	10	0	104955.3
		MyP_StrapTbl_CalTable[121]	122	10	1	105838.1
		MyP_StrapTbl_CalTable[122]	123	10	2	106720.9
		MyP_StrapTbl_CalTable[123]	124	10	3	107603.7
		MyP_StrapTbl_CalTable[124]	125	10	4	108486.5
		MyP_StrapTbl_CalTable[125]	126	10	5	109369.3
		MyP_StrapTbl_CalTable[126]	127	10	6	110252.1
		MyP_StrapTbl_CalTable[127]	128	10	7	111134.9
		MyP_StrapTbl_CalTable[128]	129	10	8	112017.7
		MyP_StrapTbl_CalTable[129]	130	10	9	112900.5
		MyP_StrapTbl_CalTable[130]	131	10	10	113783.3
		MyP_StrapTbl_CalTable[131]	132	10	11	114666.1
		MyP_StrapTbl_CalTable[132]	133	11	0	115548.9
		MyP_StrapTbl_CalTable[133]	134	11	1	116431.7
		MyP_StrapTbl_CalTable[134]	135	11	2	117314.5
		MyP_StrapTbl_CalTable[135]	136	11	3	118197.3
		MyP_StrapTbl_CalTable[136]	137	11	4	119080.1
		MyP_StrapTbl_CalTable[137]	138	11	5	119962.9
		MyP_StrapTbl_CalTable[138]	139	11	6	120845.7
		MyP_StrapTbl_CalTable[139]	140	11	7	121728.5
		MyP_StrapTbl_CalTable[140]	141	11	8	122611.3
		MyP_StrapTbl_CalTable[141]	142	11	9	123494.1
		MyP_StrapTbl_CalTable[142]	143	11	10	124376.9
		MyP_StrapTbl_CalTable[143]	144	11	11	125259.7
		MyP_StrapTbl_CalTable[144]	145	12	0	126142.5
		MyP_StrapTbl_CalTable[145]	146	12	1	127025.3
		MyP_StrapTbl_CalTable[146]	147	12	2	127908.1
		MyP_StrapTbl_CalTable[147]	148	12	3	128790.9
		MyP_StrapTbl_CalTable[148]	149	12	4	129673.7
		MyP_StrapTbl_CalTable[149]	150	12	5	130556.5
		MyP_StrapTbl_CalTable[150]	151	12	6	131439.3
		MyP_StrapTbl_CalTable[151]	152	12	7	132322.1
		MyP_StrapTbl_CalTable[152]	153	12	8	133204.9
		MyP_StrapTbl_CalTable[153]	154	12	9	134087.7
		MyP_StrapTbl_CalTable[154]	155	12	10	134970.5
		MyP_StrapTbl_CalTable[155]	156	12	11	135853.3
		MyP_StrapTbl_CalTable[156]	157	13	0	136736.1
		MyP_StrapTbl_CalTable[157]	158	13	1	137618.9
		MyP_StrapTbl_CalTable[158]	159	13	2	138501.7
		MyP_StrapTbl_CalTable[159]	160	13	3	139384.5
		MyP_StrapTbl_CalTable[160]	161	13	4	140267.3
		MyP_StrapTbl_CalTable[161]	162	13	5	141150.1
		MyP_StrapTbl_CalTable[162]	163	13	6	142032.9
		MyP_StrapTbl_CalTable[163]	164	13	7	142915.7
		MyP_StrapTbl_CalTable[164]	165	13	8	143798.5
		MyP_StrapTbl_CalTable[165]	166	13	9	144681.3
		MyP_StrapTbl_CalTable[166]	167	13	10	145564.1
		MyP_StrapTbl_CalTable[167]	168	13	11	146446.9
		MyP_StrapTbl_CalTable[168]	169	14	0	147329.7
		MyP_StrapTbl_CalTable[169]	170	14	1	148212.5
		MyP_StrapTbl_CalTable[170]	171	14	2	149095.3
		MyP_StrapTbl_CalTable[171]	172	14	3	149978.1
		MyP_StrapTbl_CalTable[172]	173	14	4	150860.9
		MyP_StrapTbl_CalTable[173]	174	14	5	151743.7
		MyP_StrapTbl_CalTable[174]	175	14	6	152626.5
		MyP_StrapTbl_CalTable[175]	176	14	7	153509.3
		MyP_StrapTbl_CalTable[176]	177	14	8	154392.1
		MyP_StrapTbl_CalTable[177]	178	14	9	155274.9
		MyP_StrapTbl_CalTable[178]	179	14	10	156157.7
		MyP_StrapTbl_CalTable[179]	180	14	11	157040.5
		MyP_StrapTbl_CalTable[180]	181	15	0	157923.3
		MyP_StrapTbl_CalTable[181]	182	15	1	158806.1
		MyP_StrapTbl_CalTable[182]	183	15	2	159688.9
		MyP_StrapTbl_CalTable[183]	184	15	3	160571.7
		MyP_StrapTbl_CalTable[184]	185	15	4	161454.5
		MyP_StrapTbl_CalTable[185]	186	15	5	162337.3
		MyP_StrapTbl_CalTable[186]	187	15	6	163220.1
		MyP_StrapTbl_CalTable[187]	188	15	7	164102.9
		MyP_StrapTbl_CalTable[188]	189	15	8	164985.7
		MyP_StrapTbl_CalTable[189]	190	15	9	165868.5
		MyP_StrapTbl_CalTable[190]	191	15	10	166751.3
		MyP_StrapTbl_CalTable[191]	192	15	11	167634.1
		MyP_StrapTbl_CalTable[192]	193	16	0	168516.9
		MyP_StrapTbl_CalTable[193]	194	16	1	169399.7
		MyP_StrapTbl_CalTable[194]	195	16	2	170282.5
		MyP_StrapTbl_CalTable[195]	196	16	3	171165.3
		MyP_StrapTbl_CalTable[196]	197	16	4	172048.1
		MyP_StrapTbl_CalTable[197]	198	16	5	172930.9
		MyP_StrapTbl_CalTable[198]	199	16	6	173813.7
		MyP_StrapTbl_CalTable[199]	200	16	7	174696.5
		MyP_StrapTbl_CalTable[200]	201	16	8	175579.3
		MyP_StrapTbl_CalTable[201]	202	16	9	176462.1
		MyP_StrapTbl_CalTable[202]	203	16	10	177344.9
		MyP_StrapTbl_CalTable[203]	204	16	11	178227.7
		MyP_StrapTbl_CalTable[204]	205	17	0	179110.5
		MyP_StrapTbl_CalTable[205]	206	17	1	179993.3
		MyP_StrapTbl_CalTable[206]	207	17	2	180876.1
		MyP_StrapTbl_CalTable[207]	208	17	3	181758.9
		MyP_StrapTbl_CalTable[208]	209	17	4	182641.7
		MyP_StrapTbl_CalTable[209]	210	17	5	183524.5
		MyP_StrapTbl_CalTable[210]	211	17	6	184407.3
		MyP_StrapTbl_CalTable[211]	212	17	7	185290.1
		MyP_StrapTbl_CalTable[212]	213	17	8	186172.9
		MyP_StrapTbl_CalTable[213]	214	17	9	187055.7
		MyP_StrapTbl_CalTable[214]	215	17	10	187938.5
		MyP_StrapTbl_CalTable[215]	216	17	11	188821.3
		MyP_StrapTbl_CalTable[216]	217	18	0	189704.1
		MyP_StrapTbl_CalTable[217]	218	18	1	190586.9
		MyP_StrapTbl_CalTable[218]	219	18	2	191469.7
		MyP_StrapTbl_CalTable[219]	220	18	3	192352.5
		MyP_StrapTbl_CalTable[220]	221	18	4	193235.3
		MyP_StrapTbl_CalTable[221]	222	18	5	194118.1
		MyP_StrapTbl_CalTable[222]	223	18	6	195000.9
		MyP_StrapTbl_CalTable[223]	224	18	7	195883.7
		MyP_StrapTbl_CalTable[224]	225	18	8	196766.5
		MyP_StrapTbl_CalTable[225]	226	18	9	197649.3
		MyP_StrapTbl_CalTable[226]	227	18	10	198532.1
		MyP_StrapTbl_CalTable[227]	228	18	11	199414.9
		MyP_StrapTbl_CalTable[228]	229	19	0	200297.7
		MyP_StrapTbl_CalTable[229]	230	19	1	201180.5
		MyP_StrapTbl_CalTable[230]	231	19	2	202063.3
		MyP_StrapTbl_CalTable[231]	232	19	3	202946.1
		MyP_StrapTbl_CalTable[232]	233	19	4	203828.9
		MyP_StrapTbl_CalTable[233]	234	19	5	204711.7
		MyP_StrapTbl_CalTable[234]	235	19	6	205594.5
		MyP_StrapTbl_CalTable[235]	236	19	7	206477.3
		MyP_StrapTbl_CalTable[236]	237	19	8	207360.1
		MyP_StrapTbl_CalTable[237]	238	19	9	208242.9
		MyP_StrapTbl_CalTable[238]	239	19	10	209125.7
		MyP_StrapTbl_CalTable[239]	240	19	11	210008.5
		MyP_StrapTbl_CalTable[240]	241	20	0	210891.3
		MyP_StrapTbl_CalTable[241]	242	20	1	211774.1
		MyP_StrapTbl_CalTable[242]	243	20	2	212656.9
		MyP_StrapTbl_CalTable[243]	244	20	3	213539.7
		MyP_StrapTbl_CalTable[244]	245	20	4	214422.5
		MyP_StrapTbl_CalTable[245]	246	20	5	215305.3
		MyP_StrapTbl_CalTable[246]	247	20	6	216188.1
		MyP_StrapTbl_CalTable[247]	248	20	7	217070.9
		MyP_StrapTbl_CalTable[248]	249	20	8	217953.7
		MyP_StrapTbl_CalTable[249]	250	20	9	218836.5
		MyP_StrapTbl_CalTable[250]	251	20	10	219719.3
		MyP_StrapTbl_CalTable[251]	252	20	11	220602.1
		MyP_StrapTbl_CalTable[252]	253	21	0	221484.9
		MyP_StrapTbl_CalTable[253]	254	21	1	222367.7
		MyP_StrapTbl_CalTable[254]	255	21	2	223250.5
		MyP_StrapTbl_CalTable[255]	256	21	3	224133.3
		MyP_StrapTbl_CalTable[256]	257	21	4	225016.1
		MyP_StrapTbl_CalTable[257]	258	21	5	225898.9
		MyP_StrapTbl_CalTable[258]	259	21	6	226781.7
		MyP_StrapTbl_CalTable[259]	260	21	7	227664.5
		MyP_StrapTbl_CalTable[260]	261	21	8	228547.3
		MyP_StrapTbl_CalTable[261]	262	21	9	229430.1
		MyP_StrapTbl_CalTable[262]	263	21	10	230312.9
		MyP_StrapTbl_CalTable[263]	264	21	11	231195.7
		MyP_StrapTbl_CalTable[264]	265	22	0	232078.5
		MyP_StrapTbl_CalTable[265]	266	22	1	232961.3
		MyP_StrapTbl_CalTable[266]	267	22	2	233844.1
		MyP_StrapTbl_CalTable[267]	268	22	3	234726.9
		MyP_StrapTbl_CalTable[268]	269	22	4	235609.7
		MyP_StrapTbl_CalTable[269]	270	22	5	236492.5
		MyP_StrapTbl_CalTable[270]	271	22	6	237375.3
		MyP_StrapTbl_CalTable[271]	272	22	7	238258.1
		MyP_StrapTbl_CalTable[272]	273	22	8	239140.9
		MyP_StrapTbl_CalTable[273]	274	22	9	240023.7
		MyP_StrapTbl_CalTable[274]	275	22	10	240906.5
		MyP_StrapTbl_CalTable[275]	276	22	11	241789.3
		MyP_StrapTbl_CalTable[276]	277	23	0	242672.1
		MyP_StrapTbl_CalTable[277]	278	23	1	243554.9
		MyP_StrapTbl_CalTable[278]	279	23	2	244437.7
		MyP_StrapTbl_CalTable[279]	280	23	3	245320.5
		MyP_StrapTbl_CalTable[280]	281	23	4	246203.3
		MyP_StrapTbl_CalTable[281]	282	23	5	247086.1
		MyP_StrapTbl_CalTable[282]	283	23	6	247968.9
		MyP_StrapTbl_CalTable[283]	284	23	7	248851.7
		MyP_StrapTbl_CalTable[284]	285	23	8	249734.5
		MyP_StrapTbl_CalTable[285]	286	23	9	250617.3
		MyP_StrapTbl_CalTable[286]	287	23	10	251500.1
		MyP_StrapTbl_CalTable[287]	288	23	11	252382.9
		MyP_StrapTbl_CalTable[288]	289	24	0	253265.7
		MyP_StrapTbl_CalTable[289]	290	24	1	254148.5
		MyP_StrapTbl_CalTable[290]	291	24	2	255031.3
		MyP_StrapTbl_CalTable[291]	292	24	3	255914.1
		MyP_StrapTbl_CalTable[292]	293	24	4	256796.9
		MyP_StrapTbl_CalTable[293]	294	24	5	257679.7
		MyP_StrapTbl_CalTable[294]	295	24	6	258562.5
		MyP_StrapTbl_CalTable[295]	296	24	7	259445.3
		MyP_StrapTbl_CalTable[296]	297	24	8	260328.1
		MyP_StrapTbl_CalTable[297]	298	24	9	261210.9
		MyP_StrapTbl_CalTable[298]	299	24	10	262093.7
		MyP_StrapTbl_CalTable[299]	300	24	11	262976.5
		MyP_StrapTbl_CalTable[300]	301	25	0	263859.3
		MyP_StrapTbl_CalTable[301]	302	25	1	264742.1
		MyP_StrapTbl_CalTable[302]	303	25	2	265624.9
		MyP_StrapTbl_CalTable[303]	304	25	3	266507.7
		MyP_StrapTbl_CalTable[304]	305	25	4	267390.5
		MyP_StrapTbl_CalTable[305]	306	25	5	268273.3
		MyP_StrapTbl_CalTable[306]	307	25	6	269156.1
		MyP_StrapTbl_CalTable[307]	308	25	7	270038.9
		MyP_StrapTbl_CalTable[308]	309	25	8	270921.7
		MyP_StrapTbl_CalTable[309]	310	25	9	271804.5
		MyP_StrapTbl_CalTable[310]	311	25	10	272687.3
		MyP_StrapTbl_CalTable[311]	312	25	11	273570.1
		MyP_StrapTbl_CalTable[312]	313	26	0	274452.9
		MyP_StrapTbl_CalTable[313]	314	26	1	275335.7
		MyP_StrapTbl_CalTable[314]	315	26	2	276218.5
		MyP_StrapTbl_CalTable[315]	316	26	3	277101.3
		MyP_StrapTbl_CalTable[316]	317	26	4	277984.1
		MyP_StrapTbl_CalTable[317]	318	26	5	278866.9
		MyP_StrapTbl_CalTable[318]	319	26	6	279749.7
		MyP_StrapTbl_CalTable[319]	320	26	7	280632.5
		MyP_StrapTbl_CalTable[320]	321	26	8	281515.3
		MyP_StrapTbl_CalTable[321]	322	26	9	282398.1
		MyP_StrapTbl_CalTable[322]	323	26	10	283280.9
		MyP_StrapTbl_CalTable[323]	324	26	11	284163.7
		MyP_StrapTbl_CalTable[324]	325	27	0	285046.5
		MyP_StrapTbl_CalTable[325]	326	27	1	285929.3
		MyP_StrapTbl_CalTable[326]	327	27	2	286812.1
		MyP_StrapTbl_CalTable[327]	328	27	3	287694.9
		MyP_StrapTbl_CalTable[328]	329	27	4	288577.7
		MyP_StrapTbl_CalTable[329]	330	27	5	289460.5
		MyP_StrapTbl_CalTable[330]	331	27	6	290343.3
		MyP_StrapTbl_CalTable[331]	332	27	7	291226.1
		MyP_StrapTbl_CalTable[332]	333	27	8	292108.9
		MyP_StrapTbl_CalTable[333]	334	27	9	292991.7
		MyP_StrapTbl_CalTable[334]	335	27	10	293874.5
		MyP_StrapTbl_CalTable[335]	336	27	11	294757.3
		MyP_StrapTbl_CalTable[336]	337	28	0	295640.1
		MyP_StrapTbl_CalTable[337]	338	28	1	296522.9
		MyP_StrapTbl_CalTable[338]	339	28	2	297405.7
		MyP_StrapTbl_CalTable[339]	340	28	3	298288.5
		MyP_StrapTbl_CalTable[340]	341	28	4	299171.3
		MyP_StrapTbl_CalTable[341]	342	28	5	300054.1
		MyP_StrapTbl_CalTable[342]	343	28	6	300936.9
		MyP_StrapTbl_CalTable[343]	344	28	7	301819.7
		MyP_StrapTbl_CalTable[344]	345	28	8	302702.5
		MyP_StrapTbl_CalTable[345]	346	28	9	303585.3
		MyP_StrapTbl_CalTable[346]	347	28	10	304468.1
		MyP_StrapTbl_CalTable[347]	348	28	11	305350.9
		MyP_StrapTbl_CalTable[348]	349	29	0	306233.7
		MyP_StrapTbl_CalTable[349]	350	29	1	307116.5
		MyP_StrapTbl_CalTable[350]	351	29	2	307999.3
		MyP_StrapTbl_CalTable[351]	352	29	3	308882.1
		MyP_StrapTbl_CalTable[352]	353	29	4	309764.9
		MyP_StrapTbl_CalTable[353]	354	29	5	310647.7
		MyP_StrapTbl_CalTable[354]	355	29	6	311530.5
		MyP_StrapTbl_CalTable[355]	356	29	7	312413.3
		MyP_StrapTbl_CalTable[356]	357	29	8	313296.1
		MyP_StrapTbl_CalTable[357]	358	29	9	314178.9
		MyP_StrapTbl_CalTable[358]	359	29	10	315061.7
		MyP_StrapTbl_CalTable[359]	360	29	11	315944.5
		MyP_StrapTbl_CalTable[360]	361	30	0	316827.3
		MyP_StrapTbl_CalTable[361]	362	30	1	317710.1
		MyP_StrapTbl_CalTable[362]	363	30	2	318592.9
		MyP_StrapTbl_CalTable[363]	364	30	3	319475.7
		MyP_StrapTbl_CalTable[364]	365	30	4	320358.5
		MyP_StrapTbl_CalTable[365]	366	30	5	321241.3
		MyP_StrapTbl_CalTable[366]	367	30	6	322124.1
		MyP_StrapTbl_CalTable[367]	368	30	7	323006.9
		MyP_StrapTbl_CalTable[368]	369	30	8	323889.7
		MyP_StrapTbl_CalTable[369]	370	30	9	324772.5
		MyP_StrapTbl_CalTable[370]	371	30	10	325655.3
		MyP_StrapTbl_CalTable[371]	372	30	11	326538.1
		MyP_StrapTbl_CalTable[372]	373	31	0	327420.9
		MyP_StrapTbl_CalTable[373]	374	31	1	328303.7
		MyP_StrapTbl_CalTable[374]	375	31	2	329186.5
		MyP_StrapTbl_CalTable[375]	376	31	3	330069.3
		MyP_StrapTbl_CalTable[376]	377	31	4	330952.1
		MyP_StrapTbl_CalTable[377]	378	31	5	331834.9
		MyP_StrapTbl_CalTable[378]	379	31	6	332717.7
		MyP_StrapTbl_CalTable[379]	380	31	7	333600.5
		MyP_StrapTbl_CalTable[380]	381	31	8	334483.3
		MyP_StrapTbl_CalTable[381]	382	31	9	335366.1
		MyP_StrapTbl_CalTable[382]	383	31	10	336248.9
		MyP_StrapTbl_CalTable[383]	384	31	11	337131.7
		MyP_StrapTbl_CalTable[384]	385	32	0	338014.5
		MyP_StrapTbl_CalTable[385]	386	32	1	338897.3
		MyP_StrapTbl_CalTable[386]	387	32	2	339780.1
		MyP_StrapTbl_CalTable[387]	388	32	3	340662.9
		MyP_StrapTbl_CalTable[388]	389	32	4	341545.7
		MyP_StrapTbl_CalTable[389]	390	32	5	342428.5
		MyP_StrapTbl_CalTable[390]	391	32	6	343311.3
		MyP_StrapTbl_CalTable[391]	392	32	7	344194.1
		MyP_StrapTbl_CalTable[392]	393	32	8	345076.9
		MyP_StrapTbl_CalTable[393]	394	32	9	345959.7
		MyP_StrapTbl_CalTable[394]	395	32	10	346842.5
		MyP_StrapTbl_CalTable[395]	396	32	11	347725.3
		MyP_StrapTbl_CalTable[396]	397	33	0	348608.1
		MyP_StrapTbl_CalTable[397]	398	33	1	349490.9
		MyP_StrapTbl_CalTable[398]	399	33	2	350373.7
		MyP_StrapTbl_CalTable[399]	400	33	3	351256.5
		MyP_StrapTbl_CalTable[400]	401	33	4	352139.3
		MyP_StrapTbl_CalTable[401]	402	33	5	353022.1
		MyP_StrapTbl_CalTable[402]	403	33	6	353904.9
		MyP_StrapTbl_CalTable[403]	404	33	7	354787.7
		MyP_StrapTbl_CalTable[404]	405	33	8	355670.5
		MyP_StrapTbl_CalTable[405]	406	33	9	356553.3
		MyP_StrapTbl_CalTable[406]	407	33	10	357436.1
		MyP_StrapTbl_CalTable[407]	408	33	11	358318.9
		MyP_StrapTbl_CalTable[408]	409	34	0	359201.7
		MyP_StrapTbl_CalTable[409]	410	34	1	360084.5
		MyP_StrapTbl_CalTable[410]	411	34	2	360967.3
		MyP_StrapTbl_CalTable[411]	412	34	3	361850.1
		MyP_StrapTbl_CalTable[412]	413	34	4	362732.9
		MyP_StrapTbl_CalTable[413]	414	34	5	363615.7
		MyP_StrapTbl_CalTable[414]	415	34	6	364498.5
		MyP_StrapTbl_CalTable[415]	416	34	7	365381.3
		MyP_StrapTbl_CalTable[416]	417	34	8	366264.1
		MyP_StrapTbl_CalTable[417]	418	34	9	367146.9
		MyP_StrapTbl_CalTable[418]	419	34	10	368029.7
		MyP_StrapTbl_CalTable[419]	420	34	11	368912.5
		MyP_StrapTbl_CalTable[420]	421	35	0	369795.3
		MyP_StrapTbl_CalTable[421]	422	35	1	370678.1
		MyP_StrapTbl_CalTable[422]	423	35	2	371560.9
		MyP_StrapTbl_CalTable[423]	424	35	3	372443.7
		MyP_StrapTbl_CalTable[424]	425	35	4	373326.5
		MyP_StrapTbl_CalTable[425]	426	35	5	374209.3
		MyP_StrapTbl_CalTable[426]	427	35	6	375092.1
		MyP_StrapTbl_CalTable[427]	428	35	7	375974.9
		MyP_StrapTbl_CalTable[428]	429	35	8	376857.7
		MyP_StrapTbl_CalTable[429]	430	35	9	377740.5
		MyP_StrapTbl_CalTable[430]	431	35	10	378623.3
		MyP_StrapTbl_CalTable[431]	432	35	11	379506.1
		MyP_StrapTbl_CalTable[432]	433	36	0	380388.9
		MyP_StrapTbl_CalTable[433]	434	36	1	381271.7
		MyP_StrapTbl_CalTable[434]	435	36	2	382154.5
		MyP_StrapTbl_CalTable[435]	436	36	3	383037.3
		MyP_StrapTbl_CalTable[436]	437	36	4	383920.1
		MyP_StrapTbl_CalTable[437]	438	36	5	384802.9
		MyP_StrapTbl_CalTable[438]	439	36	6	385685.7
		MyP_StrapTbl_CalTable[439]	440	36	7	386568.5
		MyP_StrapTbl_CalTable[440]	441	36	8	387451.3
		MyP_StrapTbl_CalTable[441]	442	36	9	388334.1
		MyP_StrapTbl_CalTable[442]	443	36	10	389216.9
		MyP_StrapTbl_CalTable[443]	444	36	11	390099.7
		MyP_StrapTbl_CalTable[444]	445	37	0	390982.5
		MyP_StrapTbl_CalTable[445]	446	37	1	390982.5
		MyP_StrapTbl_CalTable[446]	447	37	2
		MyP_StrapTbl_CalTable[447]	448	37	3
		MyP_StrapTbl_CalTable[448]	449	37	4
		MyP_StrapTbl_CalTable[449]	450	37	5
		MyP_StrapTbl_CalTable[450]	451	37	6
		MyP_StrapTbl_CalTable[451]	452	37	7
		MyP_StrapTbl_CalTable[452]	453	37	8
		MyP_StrapTbl_CalTable[453]	454	37	9
		MyP_StrapTbl_CalTable[454]	455	37	10
		MyP_StrapTbl_CalTable[455]	456	37	11
		MyP_StrapTbl_CalTable[456]	457	38	0
		MyP_StrapTbl_CalTable[457]	458	38	1
		MyP_StrapTbl_CalTable[458]	459	38	2
		MyP_StrapTbl_CalTable[459]	460	38	3
		MyP_StrapTbl_CalTable[460]	461	38	4
		MyP_StrapTbl_CalTable[461]	462	38	5
		MyP_StrapTbl_CalTable[462]	463	38	6
		MyP_StrapTbl_CalTable[463]	464	38	7
		MyP_StrapTbl_CalTable[464]	465	38	8
		MyP_StrapTbl_CalTable[465]	466	38	9
		MyP_StrapTbl_CalTable[466]	467	38	10
		MyP_StrapTbl_CalTable[467]	468	38	11
		MyP_StrapTbl_CalTable[468]	469	39	0
		MyP_StrapTbl_CalTable[469]	470	39	1
		MyP_StrapTbl_CalTable[470]	471	39	2
		MyP_StrapTbl_CalTable[471]	472	39	3
		MyP_StrapTbl_CalTable[472]	473	39	4
		MyP_StrapTbl_CalTable[473]	474	39	5
		MyP_StrapTbl_CalTable[474]	475	39	6
		MyP_StrapTbl_CalTable[475]	476	39	7
		MyP_StrapTbl_CalTable[476]	477	39	8
		MyP_StrapTbl_CalTable[477]	478	39	9
		MyP_StrapTbl_CalTable[478]	479	39	10
		MyP_StrapTbl_CalTable[479]	480	39	11
		MyP_StrapTbl_CalTable[480]	481	40	0
		MyP_StrapTbl_CalTable[481]	482	40	1
		MyP_StrapTbl_CalTable[482]	483	40	2
		MyP_StrapTbl_CalTable[483]	484	40	3
		MyP_StrapTbl_CalTable[484]	485	40	4
		MyP_StrapTbl_CalTable[485]	486	40	5
		MyP_StrapTbl_CalTable[486]	487	40	6
		MyP_StrapTbl_CalTable[487]	488	40	7
		MyP_StrapTbl_CalTable[488]	489	40	8
		MyP_StrapTbl_CalTable[489]	490	40	9
		MyP_StrapTbl_CalTable[490]	491	40	10
		MyP_StrapTbl_CalTable[491]	492	40	11
		MyP_StrapTbl_CalTable[492]	493	41	0
		MyP_StrapTbl_CalTable[493]	494	41	1
		MyP_StrapTbl_CalTable[494]	495	41	2
		MyP_StrapTbl_CalTable[495]	496	41	3
		MyP_StrapTbl_CalTable[496]	497	41	4
		MyP_StrapTbl_CalTable[497]	498	41	5
		MyP_StrapTbl_CalTable[498]	499	41	6
		MyP_StrapTbl_CalTable[499]	500	41	7
		MyP_StrapTbl_CalTable[500]	501	41	8
		MyP_StrapTbl_CalTable[501]	502	41	9
		MyP_StrapTbl_CalTable[502]	503	41	10
		MyP_StrapTbl_CalTable[503]	504	41	11
		MyP_StrapTbl_CalTable[504]	505	42	0
		MyP_StrapTbl_CalTable[505]	506	42	1
		MyP_StrapTbl_CalTable[506]	507	42	2
		MyP_StrapTbl_CalTable[507]	508	42	3
		MyP_StrapTbl_CalTable[508]	509	42	4
		MyP_StrapTbl_CalTable[509]	510	42	5
		MyP_StrapTbl_CalTable[510]	511	42	6
		MyP_StrapTbl_CalTable[511]	512	42	7
		MyP_StrapTbl_CalTable[512]	513	42	8
		MyP_StrapTbl_CalTable[513]	514	42	9
		MyP_StrapTbl_CalTable[514]	515	42	10
		MyP_StrapTbl_CalTable[515]	516	42	11
		MyP_StrapTbl_CalTable[516]	517	43	0
		MyP_StrapTbl_CalTable[517]	518	43	1
		MyP_StrapTbl_CalTable[518]	519	43	2
		MyP_StrapTbl_CalTable[519]	520	43	3
		MyP_StrapTbl_CalTable[520]	521	43	4
		MyP_StrapTbl_CalTable[521]	522	43	5
		MyP_StrapTbl_CalTable[522]	523	43	6
		MyP_StrapTbl_CalTable[523]	524	43	7
		MyP_StrapTbl_CalTable[524]	525	43	8
		MyP_StrapTbl_CalTable[525]	526	43	9
		MyP_StrapTbl_CalTable[526]	527	43	10
		MyP_StrapTbl_CalTable[527]	528	43	11
		MyP_StrapTbl_CalTable[528]	529	44	0
		MyP_StrapTbl_CalTable[529]	530	44	1
		MyP_StrapTbl_CalTable[530]	531	44	2
		MyP_StrapTbl_CalTable[531]	532	44	3
		MyP_StrapTbl_CalTable[532]	533	44	4
		MyP_StrapTbl_CalTable[533]	534	44	5
		MyP_StrapTbl_CalTable[534]	535	44	6
		MyP_StrapTbl_CalTable[535]	536	44	7
		MyP_StrapTbl_CalTable[536]	537	44	8
		MyP_StrapTbl_CalTable[537]	538	44	9
		MyP_StrapTbl_CalTable[538]	539	44	10
		MyP_StrapTbl_CalTable[539]	540	44	11
		MyP_StrapTbl_CalTable[540]	541	45	0
		MyP_StrapTbl_CalTable[541]	542	45	1
		MyP_StrapTbl_CalTable[542]	543	45	2
		MyP_StrapTbl_CalTable[543]	544	45	3
		MyP_StrapTbl_CalTable[544]	545	45	4
		MyP_StrapTbl_CalTable[545]	546	45	5
		MyP_StrapTbl_CalTable[546]	547	45	6
		MyP_StrapTbl_CalTable[547]	548	45	7
		MyP_StrapTbl_CalTable[548]	549	45	8
		MyP_StrapTbl_CalTable[549]	550	45	9
		MyP_StrapTbl_CalTable[550]	551	45	10
		MyP_StrapTbl_CalTable[551]	552	45	11
		MyP_StrapTbl_CalTable[552]	553	46	0
		MyP_StrapTbl_CalTable[553]	554	46	1
		MyP_StrapTbl_CalTable[554]	555	46	2
		MyP_StrapTbl_CalTable[555]	556	46	3
		MyP_StrapTbl_CalTable[556]	557	46	4
		MyP_StrapTbl_CalTable[557]	558	46	5
		MyP_StrapTbl_CalTable[558]	559	46	6
		MyP_StrapTbl_CalTable[559]	560	46	7
		MyP_StrapTbl_CalTable[560]	561	46	8
		MyP_StrapTbl_CalTable[561]	562	46	9
		MyP_StrapTbl_CalTable[562]	563	46	10
		MyP_StrapTbl_CalTable[563]	564	46	11
		MyP_StrapTbl_CalTable[564]	565	47	0
		MyP_StrapTbl_CalTable[565]	566	47	1
		MyP_StrapTbl_CalTable[566]	567	47	2
		MyP_StrapTbl_CalTable[567]	568	47	3
		MyP_StrapTbl_CalTable[568]	569	47	4
		MyP_StrapTbl_CalTable[569]	570	47	5
		MyP_StrapTbl_CalTable[570]	571	47	6
		MyP_StrapTbl_CalTable[571]	572	47	7
		MyP_StrapTbl_CalTable[572]	573	47	8
		MyP_StrapTbl_CalTable[573]	574	47	9
		MyP_StrapTbl_CalTable[574]	575	47	10
		MyP_StrapTbl_CalTable[575]	576	47	11
		MyP_StrapTbl_CalTable[576]	577	48	0
		MyP_StrapTbl_CalTable[577]	578	48	1
		MyP_StrapTbl_CalTable[578]	579	48	2
		MyP_StrapTbl_CalTable[579]	580	48	3
		MyP_StrapTbl_CalTable[580]	581	48	4
		MyP_StrapTbl_CalTable[581]	582	48	5
		MyP_StrapTbl_CalTable[582]	583	48	6
		MyP_StrapTbl_CalTable[583]	584	48	7
		MyP_StrapTbl_CalTable[584]	585	48	8
		MyP_StrapTbl_CalTable[585]	586	48	9
		MyP_StrapTbl_CalTable[586]	587	48	10
		MyP_StrapTbl_CalTable[587]	588	48	11
		MyP_StrapTbl_CalTable[588]	589	49	0
		MyP_StrapTbl_CalTable[589]	590	49	1
		MyP_StrapTbl_CalTable[590]	591	49	2
		MyP_StrapTbl_CalTable[591]	592	49	3
		MyP_StrapTbl_CalTable[592]	593	49	4
		MyP_StrapTbl_CalTable[593]	594	49	5
		MyP_StrapTbl_CalTable[594]	595	49	6
		MyP_StrapTbl_CalTable[595]	596	49	7
		MyP_StrapTbl_CalTable[596]	597	49	8
		MyP_StrapTbl_CalTable[597]	598	49	9
		MyP_StrapTbl_CalTable[598]	599	49	10
		MyP_StrapTbl_CalTable[599]	600	49	11
		MyP_StrapTbl_CalTable[600]	601	50	0